## ANNEXURE X_BHP_TS
[5 empty] | ANNEXURE-X: | ANNEXURE-IX
TOWER SCHEDULE FOR ASSOCIATED TRANSMISSION LINE FOR 220/33KV BIHPURIA GIS
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN ( M ) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN ( HOT) |  |  | WEIGHT SPAN IN ( COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
1 | BAY | BAY | Gantry | 0 | [5 empty] | 72.28 | 0 |  | 51 |  | -4.7498 | -4.7498 |  | -33.4123 | -33.4123 |  |  | VILL-PABHOI | 93°9'16.1" | 26°48'25.7"
[7 empty] | 51 |  |  |  |  | 0.85 | [8 empty] | S/S Boundary
2 | 1 | 1/0 | DD+3 | 3 |  | 06°24'59"RT |  | 51 | 51 | 70.13 | 0 |  | 401 | 55.7498 | 159.1318 | 214.8816 | 84.4123 | 144.0963 | 228.5086 |  |  | VILL-PABHOI | 93°9'18" | 26°48'25.8"
[7 empty] | 350 |  |  |  |  | 3.06 | [8 empty] | 11Kv
3 |  | 1/1 | DA+6 | 6 | [5 empty] | 70.19 | 0 |  | 700 | 190.8682 | 206.1659 | 397.0341 | 205.9037 | 235.6965 | 441.6002 |  |  |  | 93°9'30.7" | 26°48'25.4"
[7 empty] | 350 |  |  |  |  | -6.01 | [8 empty] | Foot Track, Canal, Tea Garden
4 |  | 1/2 | DA+0 | 0 | [5 empty] | 70.18 | 0 |  | 658 | 143.8341 | 135.6733 | 279.5074 | 114.3035 | 118.3083 | 232.6118 |  |  |  | 93°9'43.4" | 26°48'25"
[7 empty] | 308 |  |  |  |  | 3.11 | [8 empty] | Tea Garden, Drain, LT Line, Metal Road, Vill Road
5 | 2 | 2/0 | DB+3 | 3 |  | 02°18'46"RT |  | 1008 | 1059 | 70.29 | 0 |  | 565 | 172.3267 | 151.0285 | 323.3551 | 189.6917 | 172.3748 | 362.0664 |  |  | VILL-GEREKI | 93°9'54.5" | 26°48'24.7"
[7 empty] | 257 |  |  |  |  | -3.19 | [8 empty] | Drain
6 | 3 | 3/0 | DC+0 | 0 |  | 24°02'02"LT |  | 257 | 1316 | 70.1 | 0 |  | 484 | 105.9715 | 110.3817 | 216.3533 | 84.6252 | 107.4271 | 192.0523 |  |  | VILL-GEREKI | 93°10'3.8" | 26°48'24.1"
[7 empty] | 227 |  |  |  |  | 0.39
7 | 4 | 4/0 | DD+0 | 0 |  | 17°22'30"LT |  | 227 | 1543 | 70.49 | 0 |  | 326 | 116.6183 | 109.4496 | 226.0679 | 119.5729 | 166.2535 | 285.8264 |  |  | VILL-GEREKI | 93°10'11.5" | 26°48'26.6"
[7 empty] | 99 |  |  |  |  | -3.27
8 |  | 4/1 | Gantry | -3.59 |  |  |  | 99 | 1642 | 70.81 | 0 |  | 159 | -10.4496 | 32.1175 | 21.6679 | -67.2535 | 34.1239 | -33.1296 |  |  |  | 93°10'14.4" | 26°48'28.5"
[7 empty] | 60 |  |  |  |  | -0.07 | [8 empty] | 400KV D/C Biswanath Chariali - Balipara T/L.
9 |  | 4/2 | Gantry | -3.59 |  |  |  | 60 | 1702 | 70.74 | 0 |  | 134 | 27.8825 | -67.7297 | -39.8472 | 25.8761 | -166.964 | -141.0878 |  |  |  | 93°10'16.1" | 26°48'29.7"
[7 empty] | 74 |  |  |  |  | 4.27 | [8 empty] | Tea Garden
10 | 5 | 5/0 | DD+0 | 0 |  | 35°30'50"LT |  | 74 | 1776 | 71.42 | 0 |  | 286 | 141.7297 | 96.8394 | 238.5692 | 240.964 | 88.1596 | 329.1235 |  |  | VILL-GEREKI | 93°10'18.3" | 26°48'31.1"
[7 empty] | 212 |  |  |  |  | 1.07 | [8 empty] | Tea Garden
11 | 6 | 6/0 | DC+0 | 0 |  | 20°19'33"RT |  | 212 | 1988 | 72.49 | 0 |  | 300 | 115.1606 | 46.2687 | 161.4293 | 123.8404 | 48.4184 | 172.2588 |  |  | VILL-GEREKI | 93°10'20.6" | 26°48'37.7"
[7 empty] | 88 |  |  |  |  | -0.11
12 | 7 | 7/0 | DD+0 | 0 |  | 23°38'28"RT |  | 88 | 2076 | 72.38 | 0 |  | 178 | 41.7313 | 120.0195 | 161.7508 | 39.5816 | 191.1025 | 230.6841 |  |  | VILL-GEREKI | 93°10'22.5" | 26°48'40"
[7 empty] | 90 |  |  |  |  | -3.72
13 |  | 7/1 | Gantry | -3.59 |  |  |  | 90 | 2166 | 72.25 | 0 |  | 153 | -30.0195 | 30.9238 | 0.9043 | -101.1025 | 30.3779 | -70.7247 |  |  |  | 93°10'25.4" | 26°48'41.4"
[7 empty] | 63 |  |  |  |  | 0.02 | [8 empty] | 400KV D/C RNG - Biswanath Chariali T/L.
14 |  | 7/2 | Gantry | -3.59 |  |  |  | 63 | 2229 | 72.27 | 0 |  | 137 | 32.0762 | -53.0136 | -20.9374 | 32.6221 | -138.3039 | -105.6818 |  |  |  | 93°10'27.4" | 26°48'42.3"
[7 empty] | 74 |  |  |  |  | 3.67
15 | 8 | 8/0 | DD+0 | 0 |  | 07°56'41"RT |  | 74 | 2303 | 72.35 | 0 |  | 393 | 127.0136 | 86.047 | 213.0606 | 212.3039 | 16.4484 | 228.7523 |  |  | VILL-GEREKI | 93°10'29.7" | 26°48'43.5"
[7 empty] | 319 |  |  |  |  | 12.91 | [8 empty] | 3 Nos 11Kv, 2 NosFP
16 | 9 | 9/0 | DD+12 | 12 |  | 16°15'12"LT |  | 319 | 2622 | 73.26 | 0 |  | 472 | 232.953 | 18.4916 | 251.4445 | 302.5516 | -36.473 | 266.0786 |  |  | VILL-BAPUJAR | 93°10'40.5" | 26°48'47.2"
[7 empty] | 153 |  |  |  |  | 4.89 | [8 empty] | 132KV D/CBiswanath Chariali - Biswanath Chariali T/L. , LT Line, Foot Track, Tea Garden
17 | 10 | 10/0 | DD+18 | 18 |  | 27°31'49"RT |  | 153 | 2775 | 72.15 | 0 |  | 499 | 134.5084 | 240.0392 | 374.5476 | 189.473 | 303.5606 | 493.0336 |  |  | VILL-BAPUJAR | 93°10'45" | 26°48'50.1"
[7 empty] | 346 |  |  |  |  | -12.78 | [8 empty] | Tea Garden, Nala, Pond
18 | 11 | 11/0 | DD+6 | 6 |  | 34°01'54"RT |  | 346 | 3121 | 71.37 | 0 |  | 678 | 105.9608 | 183.1112 | 289.072 | 42.4394 | 199.3245 | 241.7639 |  |  | VILL-BAPUJAR | 93°10'57.3" | 26°48'52"
[7 empty] | 332 |  |  |  |  | -3.13 | [8 empty] | FP
19 |  | 11/1 | DA+3 | 3 | [5 empty] | 71.24 | 0 |  | 663 | 148.8888 | 156.2331 | 305.122 | 132.6755 | 147.4525 | 280.1281 |  |  |  | 93°11'8.2" | 26°48'47.5"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN ( M ) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN ( HOT) |  |  | WEIGHT SPAN IN ( COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
19 |  | 11/1 | DA+3 | 3 | [5 empty] | 71.24 | 0 |  | 663 | 148.8888 | 156.2331 | 305.122 | 132.6755 | 147.4525 | 280.1281 |  |  |  | 93°11'8.2" | 26°48'47.5"
[7 empty] | 331 |  |  |  |  | 1.69 | [8 empty] | Metal Road, 11Kv
20 |  | 11/2 | DA+6 | 6 | [5 empty] | 69.93 | 0 |  | 681 | 174.7669 | 198.18 | 372.9469 | 183.5475 | 220.1437 | 403.6911 |  |  |  | 93°11'19.1" | 26°48'43"
[7 empty] | 350 |  |  |  |  | -4.47 | [8 empty] | Foot Track
21 | 12 | 12/0 | DC+0 | 0 |  | 18°46'20"LT |  | 1013 | 4134 | 71.46 | 0 |  | 675 | 151.82 | 163.3935 | 315.2135 | 129.8563 | 164.2402 | 294.0965 |  |  | VILL-KALA PANI | 93°11'30.7" | 26°48'38.3"
[7 empty] | 325 |  |  |  |  | -0.16
22 |  | 12/1 | DA+0 | 0 | [5 empty] | 71.3 | 0 |  | 645 | 161.6065 | 159.603 | 321.2094 | 160.7598 | 159.2268 | 319.9866 |  |  |  | 93°11'42.4" | 26°48'37.2"
[7 empty] | 320 |  |  |  |  | 0.07 | [8 empty] | Vill Road, Burigang River, Nala
23 |  | 12/2 | DA+0 | 0 | [5 empty] | 71.37 | 0 |  | 640 | 160.397 | 165.2748 | 325.6718 | 160.7732 | 170.2728 | 331.0461 |  |  |  | 93°11'53.9" | 26°48'36.1"
[7 empty] | 320 |  |  |  |  | -0.93 | [8 empty] | Nala
24 |  | 12/3 | DA+0 | 0 | [5 empty] | 70.44 | 0 |  | 637 | 154.7252 | 142.354 | 297.0792 | 149.7272 | 127.0553 | 276.7825 |  |  |  | 93°12'5.4" | 26°48'35.1"
[7 empty] | 317 |  |  |  |  | 2.82 | [8 empty] | Abondoned Shed
25 |  | 12/4 | DA+0 | 0 | [5 empty] | 73.26 | 0 |  | 568 | 174.646 | 131.8633 | 306.5093 | 189.9447 | 137.8927 | 327.8374 |  |  |  | 93°12'16.8" | 26°48'34"
[7 empty] | 251 |  |  |  |  | -0.88 | [8 empty] | Vill Road
26 | 13 | 13/0 | DC+0 | 0 |  | 28°18'27"LT |  | 1533 | 5667 | 72.38 | 0 |  | 598 | 119.1367 | 156.867 | 276.0037 | 113.1073 | 141.1067 | 254.214 |  |  | VILL-3NO PULISOMANI | 93°12'25.9" | 26°48'33.2"
[7 empty] | 347 |  |  |  |  | 3.18
27 |  | 13/1 | DA+3 | 3 | [5 empty] | 72.56 | 0 |  | 694 | 190.133 | 179.0966 | 369.2297 | 205.8933 | 184.3996 | 390.2929 |  |  |  | 93°12'37.5" | 26°48'37.5"
[7 empty] | 347 |  |  |  |  | -1.07 | [8 empty] | Vill Road
28 | 14 | 14/0 | DB+0 | 0 |  | 03°19'03"RT |  | 694 | 6361 | 74.49 | 0 |  | 693 | 167.9034 | 162.3514 | 330.2547 | 162.6004 | 152.2615 | 314.8619 |  |  | VILL-3NO PULISOMANI | 93°12'49.1" | 26°48'41.8"
[7 empty] | 346 |  |  |  |  | 2.03 | [8 empty] | Vill Road, Hut, FP, U/C Pole
29 | 15 | 15/0 | DC+3 | 3 |  | 18°54'37"LT |  | 346 | 6707 | 73.52 | 0 |  | 701 | 183.6486 | 189.4636 | 373.1122 | 193.7385 | 200.7994 | 394.5379 |  |  | VILL-3NO PULISOMANI | 93°13'1" | 26°48'45.5"
[7 empty] | 355 |  |  |  |  | -2.34 | [8 empty] | Hut, Tea Garden, FP, Canal, Foot Track
30 | 16 | 16/0 | DC+0 | 0 |  | 21°38'39"LT |  | 355 | 7062 | 74.18 | 0 |  | 665 | 165.5364 | 155.5855 | 321.1219 | 154.2006 | 156.1402 | 310.3408 |  |  | VILL-1 NO PULISOMANI | 93°13'11.1" | 26°48'52.6"
[7 empty] | 310 |  |  |  |  | -0.1
31 |  | 16/1 | DA+0 | 0 | [5 empty] | 74.08 | 0 |  | 622 | 154.4145 | 156.0582 | 310.4727 | 153.8598 | 156.1133 | 309.9731 |  |  |  | 93°13'16.8" | 26°49'1.3"
[7 empty] | 312 |  |  |  |  | -0.01
32 |  | 16/2 | DA+0 | 0 | [5 empty] | 74.07 | 0 |  | 635 | 155.9418 | 142.8444 | 298.7862 | 155.8867 | 125.1677 | 281.0544 |  |  |  | 93°13'22.5" | 26°49'10"
[7 empty] | 323 |  |  |  |  | 3.32 | [8 empty] | 11Kv
33 | 17 | 17/0 | DB+3 | 3 |  | 5°55'48"LT |  | 945 | 8007 | 74.39 | 0 |  | 658 | 180.1556 | 184.0245 | 364.1801 | 197.8323 | 199.6819 | 397.5142 |  |  | VILL-1 NO PULISOMANI | 93°13'28.4" | 26°49'19.1"
[7 empty] | 335 |  |  |  |  | -3.05 | [8 empty] | 2 Nos Vill Road, Tea Garden
34 |  | 17/1 | DB+0 | 0 | Used DB tower instead of DA due to Single Span limit crossed |  |  | 335 | 8342 | 74.34 | 0 |  | 735 | 150.9755 | 147.7737 | 298.7492 | 135.3181 | 98.2879 | 233.606 |  |  |  | 93°13'33.4" | 26°49'29"
[7 empty] | 400 |  |  |  |  | 11.51 | [8 empty] | Tea Garden
35 |  | 17/2 | DD+12 | 12 |  |  |  | 400 | 8742 | 73.85 | 0 |  | 600 | 252.2263 | 92.9215 | 345.1478 | 301.7121 | 86.2145 | 387.9266 |  |  |  | 93°13'39.4" | 26°49'40.9"
[7 empty] | 200 |  |  |  |  | 0.78 | [8 empty] | 132 Kv D/c Biswanath Chariali - Gohpur T/L., SH-45, 33Kv
36 |  | 17/3 | DD+12 | 12 |  |  |  | 200 | 8942 | 74.63 | 0 |  | 416 | 107.0785 | 184.7169 | 291.7953 | 113.7855 | 257.4082 | 371.1936 |  |  |  | 93°13'42.4" | 26°49'46.8"
[7 empty] | 216 |  |  |  |  | -9.13
37 | 18 | 18/0 | DD+3 | 3 |  | 32°4'42"RT |  | 216 | 9158 | 74.5 | 0 |  | 216 | 31.2831 | 186.0974 | 217.3805 | -41.4082 | 196.6124 | 155.2042 |  |  | VILL-GINGIA | 93°13'45.6" | 26°49'53.2"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN ( M ) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN ( HOT) |  |  | WEIGHT SPAN IN ( COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
37 | 18 | 18/0 | DD+3 | 3 |  | 32°4'42"RT |  |  |  | 74.5 | 0 |  | 566 | 31.2831 | 186.0974 | 217.3805 | -41.4082 | 196.6124 | 155.2042 |  |  | VILL-GINGIA | 93°13'45.6" | 26°49'53.2"
[7 empty] | 350 |  |  |  |  | -2.14 | [8 empty] | Tea Garden
38 |  | 18/1 | DA+0 | 0 | [5 empty] | 75.36 | 0 |  | 700 | 163.9026 | 139.0632 | 302.9659 | 153.3876 | 105.0122 | 258.3998 |  |  |  | 93°13'56.2" | 26°49'59.5"
[7 empty] | 350 |  |  |  |  | 6.93 | [8 empty] | Tea Garden, Foot Track, Nala
39 | 19 | 19/0 | DB+6 | 6 |  | 13°22'20"RT |  | 700 | 9858 | 76.29 | 0 |  | 691 | 210.9368 | 170.4468 | 381.3835 | 244.9878 | 170.3963 | 415.3842 |  |  | VILL-UTTAR GINGIA | 93°14'6.7" | 26°50'5.8"
[7 empty] | 341 |  |  |  |  | 0.01 | [8 empty] | Tea Garden, Metal Road, 11Kv
40 |  | 19/1 | DA+6 | 6 | [5 empty] | 76.3 | 0 |  | 691 | 170.5532 | 206.6327 | 377.1859 | 170.6037 | 236.6054 | 407.2091 |  |  |  | 93°14'18.4" | 26°50'9.6"
[7 empty] | 350 |  |  |  |  | -6.1 | [8 empty] | LT Line, House
41 | 20 | 20/0 | DB+0 | 0 |  | 9°9'33"RT |  | 691 | 10549 | 76.2 | 0 |  | 697 | 143.3673 | 167.1711 | 310.5384 | 113.3946 | 161.1743 | 274.5688 |  |  | VILL-UTTAR GINGIA | 93°14'30.3" | 26°50'13.5"
[7 empty] | 347 |  |  |  |  | 1.21
42 |  | 20/1 | DA+3 | 3 | [5 empty] | 74.41 | 0 |  | 697 | 179.8289 | 189.0013 | 368.8303 | 185.8257 | 202.268 | 388.0937 |  |  |  | 93°14'42.6" | 26°50'15.6"
[7 empty] | 350 |  |  |  |  | -2.7 | [8 empty] | Pond
43 |  | 20/2 | DA+0 | 0 | [5 empty] | 74.71 | 0 |  | 692 | 160.9987 | 152.0541 | 313.0527 | 147.732 | 134.1023 | 281.8343 |  |  |  | 93°14'55" | 26°50'17.8"
[7 empty] | 342 |  |  |  |  | 3.57 | [8 empty] | Tea Garden, Pond, Nala
44 |  | 20/3 | DA+3 | 3 | [5 empty] | 75.28 | 0 |  | 689 | 189.9459 | 168.3741 | 358.32 | 207.8977 | 163.5172 | 371.4149 |  |  |  | 93°15'7.2" | 26°50'19.9"
[7 empty] | 347 |  |  |  |  | 0.98 | [8 empty] | Tea Garden , Shed, Hut
45 | 21 | 21/0 | DC+3 | 3 |  | 18°20'08"RT |  | 1386 | 11935 | 76.26 | 0 |  | 652 | 178.6259 | 157.9152 | 336.5411 | 183.4828 | 163.0463 | 346.5291 |  |  | VILL-SOLMARI | 93°15'19.5" | 26°50'22.1"
[7 empty] | 305 |  |  |  |  | -0.91 | [8 empty] | Tea Garden, 11Kv, Metal Road
46 | 22 | 22/0 | DB+3 | 3 |  | 13°41'13"LT |  | 305 | 12240 | 75.35 | 0 |  | 683 | 147.0848 | 184.8707 | 331.9555 | 141.9537 | 180.958 | 322.9117 |  |  | VILL-SOLMARI | 93°15'30.5" | 26°50'20.8"
[7 empty] | 378 |  |  |  |  | 0.86 | [8 empty] | 11 Kv
47 | 23 | 23/0 | DB+3 | 3 |  | 05°13'26"LT |  | 378 | 12618 | 76.21 | 0 |  | 706 | 193.1293 | 174.1263 | 367.2556 | 197.042 | 183.7213 | 380.7633 |  |  | VILL-SOLMARI | 93°15'44.1" | 26°50'22.2"
[7 empty] | 328 |  |  |  |  | -1.83 | [8 empty] | Shed, Hut, Vill Road, LT Line, Tea Garden
48 |  | 23/1 | DA+0 | 0 | [5 empty] | 77.38 | 0 |  | 593 | 153.8737 | 152.2252 | 306.0988 | 144.2787 | 170.9153 | 315.194 |  |  |  | 93°15'55.8" | 26°50'24.3"
[7 empty] | 265 |  |  |  |  | -2.88 | [8 empty] | Tea Garden , Vill Road
49 | 24 | 24/0 | DD+0 | 0 |  | 35°32'31"LT |  | 593 | 13211 | 74.5 | 0 |  | 537 | 112.7748 | 135.0658 | 247.8407 | 94.0847 | 134.1806 | 228.2654 |  |  | VILL-SOLMARI | 93°16'5.2" | 26°50'26"
[7 empty] | 272 |  |  |  |  | 0.14 | [8 empty] | Tea Garden
50 |  | 24/1 | DA+0 | 0 | [5 empty] | 74.64 | 0 |  | 549 | 136.9342 | 134.6341 | 271.5683 | 137.8194 | 130.9711 | 268.7905 |  |  |  | 93°16'11.9" | 26°50'32.5"
[7 empty] | 277 |  |  |  |  | 0.59 | [8 empty] | Tea Garden, Nala
51 |  | 24/2 | DA+0 | 0 | [5 empty] | 75.23 | 0 |  | 569 | 142.3659 | 131.8903 | 274.2562 | 146.0289 | 118.521 | 264.5499 |  |  |  | 93°16'18.7" | 26°50'39.1"
[7 empty] | 292 |  |  |  |  | 2.27 | [8 empty] | Tea Garden, Foot Track
52 |  | 24/3 | DB+3 | 3 |  |  |  | 841 | 14052 | 74.5 | 0 |  | 642 | 160.1097 | 123.7655 | 283.8751 | 173.479 | 75.2194 | 248.6983 |  |  |  | 93°16'25.9" | 26°50'46"
[7 empty] | 350 |  |  |  |  | 9.88
53 | 25 | 25/0 | DD+12 | 12 |  | 21°28'22"RT |  | 350 | 14402 | 75.38 | 0 |  | 877 | 226.2345 | 246.3833 | 472.6178 | 274.7806 | 230.1648 | 504.9454 |  |  | VILL-SOLMARI | 93°16'34.5" | 26°50'54.4"
[7 empty] | 527 |  |  |  |  | 4.97 | [8 empty] | Barigang River, Tea Garden
54 | 26 | 26/0 | DD+9 | 9 |  | 38°50'25"LT |  | 527 | 14929 | 83.35 | 0 |  | 871 | 280.6167 | 197.8003 | 478.417 | 296.8352 | 222.2467 | 519.0819 |  |  | VILL-BARGANG | 93°16'51.8" | 26°51'1.8"
[7 empty] | 344 |  |  |  |  | -4.89 | [8 empty] | Tea Garden , Foot Track
55 |  | 26/1 | DA+3 | 3 | [5 empty] | 84.46 | 0 |  | 344 | 146.1997 | 166.3399 | 312.5396 | 121.7533 | 158.1342 | 279.8875 |  |  |  | 93°16'57.1" | 26°51'11.9"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN ( M ) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN ( HOT) |  |  | WEIGHT SPAN IN ( COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
55 |  | 26/1 | DA+3 | 3 | [5 empty] | 84.46 | 0 |  | 694 | 146.1997 | 166.3399 | 312.5396 | 121.7533 | 158.1342 | 279.8875 |  |  |  | 93°16'57.1" | 26°51'11.9"
[7 empty] | 350 |  |  |  |  | 1.67 | [8 empty] | Tea Garden, Nala, Foot Track. Vill Road, 11Kv
56 | 27 | 27/0 | DB+3 | 3 |  | 14°38'11"LT |  | 694 | 15623 | 86.13 | 0 |  | 692 | 183.6601 | 181.4548 | 365.1148 | 191.8658 | 191.3609 | 383.2267 |  |  | VILL-BARGANG | 93°17'2.6" | 26°51'22.1"
[7 empty] | 342 |  |  |  |  | -1.97 | [8 empty] | 2 Nos Tea Garden, Rubber Garden, Pond
57 | 28 | 28/0 | DD+0 | 0 |  | 37°08'41"RT |  | 342 | 15965 | 87.16 | 0 |  | 494 | 160.5452 | 71.5819 | 232.1272 | 150.6391 | 67.3957 | 218.0348 |  |  | VILL-BARGANG | 93°17'5" | 26°51'33"
[7 empty] | 152 |  |  |  |  | 0.37 | [8 empty] | Rubber Garden, Tea Garden
58 | 29 | 29/0 | DD+0 | 0 |  | 21°49'58"RT |  | 152 | 16117 | 87.53 | 0 |  | 231 | 80.4181 | 108.1939 | 188.6119 | 84.6043 | 173.2831 | 257.8874 |  |  | VILL-BARGANG | 93°17'9.1" | 26°51'36.4"
[7 empty] | 79 |  |  |  |  | -2.99 | [8 empty] | Tea Garden
59 |  | 29/1 | Gantry | -3.59 |  |  |  | 79 | 16196 | 88.13 | 0 |  | 139 | -29.1939 | 37.5625 | 8.3686 | -94.2831 | 44.7281 | -49.5551 |  |  |  | 93°17'11.8" | 26°51'37.2"
[7 empty] | 60 |  |  |  |  | -0.25 | [8 empty] | 400 Kv D/C Ranganadi - Balipara T/L.
60 |  | 29/2 | Gantry | -3.59 |  |  |  | 60 | 16256 | 87.88 | 0 |  | 131 | 22.4375 | 11.9818 | 34.4194 | 15.2719 | -10.3022 | 4.9697 |  |  |  | 93°17'13.8" | 26°51'37.9"
[7 empty] | 71 |  |  |  |  | 0.92 | [8 empty] | Hut
61 | 30 | 30/0 | DD+0 | 0 |  | 16°33'22"RT |  | 71 | 16327 | 85.21 | 0 |  | 273 | 59.0182 | 72.4274 | 131.4456 | 81.3022 | 45.3541 | 126.6564 |  |  | VILL-BARGANG | 93°17'16.3" | 26°51'38.7"
[7 empty] | 202 |  |  |  |  | 3.18 | [8 empty] | Sukhan Kuti River, Tea Garden
62 | 31 | 31/0 | DB+0 | 0 |  | 07°26'03"RT |  | 202 | 16529 | 88.39 | 0 |  | 522 | 129.5726 | 157.788 | 287.3606 | 156.6459 | 155.692 | 312.3379 |  |  | VILL-BARGANG | 93°17'23.6" | 26°51'39.1"
[7 empty] | 320 |  |  |  |  | 0.39 | [8 empty] | Drain, 2 NosFoot Track, Tea Garden, 2Nos Nala
63 |  | 31/1 | DA+0 | 0 | [5 empty] | 88.78 | 0 |  | 620 | 162.212 | 150.726 | 312.938 | 164.308 | 151.4139 | 315.7219 |  |  |  | 93°17'35.1" | 26°51'38.4"
[7 empty] | 300 |  |  |  |  | -0.12 | [8 empty] | 2 Nos Drain, 2 Nos Foot Track, Tea Garden
64 |  | 31/2 | DA+0 | 0 | [5 empty] | 88.66 | 0 |  | 600 | 149.274 | 155.1425 | 304.4165 | 148.5861 | 160.0151 | 308.6012 |  |  |  | 93°17'46" | 26°51'37.8"
[7 empty] | 300 |  |  |  |  | -0.85 | [8 empty] | Foot Track, Tea Garden, 3 Nos Nala
65 |  | 31/3 | DA+0 | 0 | [5 empty] | 87.81 | 0 |  | 620 | 144.8575 | 157.1641 | 302.0216 | 139.9849 | 154.477 | 294.4619 |  |  |  | 93°17'56.8" | 26°51'37.1"
[7 empty] | 320 |  |  |  |  | 0.5 | [8 empty] | FP, Nala, Foot Track, Tea Garden, Drain
66 |  | 31/4 | DA+0 | 0 | [5 empty] | 88.31 | 0 |  | 595 | 162.8359 | 138.028 | 300.8639 | 165.523 | 138.5283 | 304.0513 |  |  |  | 93°18'8.4" | 26°51'36.4"
[7 empty] | 275 |  |  |  |  | -0.08 | [8 empty] | Tea Garden, Foot Track, Metal Road, 11Kv
67 |  | 31/5 | DA+0 | 0 | [5 empty] | 88.23 | 0 |  | 575 | 136.972 | 150.7865 | 287.7585 | 136.4717 | 151.5317 | 288.0034 |  |  |  | 93°18'18.4" | 26°51'35.8"
[7 empty] | 300 |  |  |  |  | -0.13 | [8 empty] | 2 Nos Nala, Tea Garden, Foot Track
68 |  | 31/6 | DA+0 | 0 | [5 empty] | 88.1 | 0 |  | 620 | 149.2135 | 143.2681 | 292.4816 | 148.4683 | 127.4141 | 275.8824 |  |  |  | 93°18'29.2" | 26°51'35.1"
[7 empty] | 320 |  |  |  |  | 2.95 | [8 empty] | Tea Garden, 3Nos Nala, 11Kv, Foot Track
69 |  | 31/7 | DA+3 | 3 | [5 empty] | 88.05 | 0 |  | 640 | 176.7319 | 177.9797 | 354.7117 | 192.5859 | 195.016 | 387.6019 |  |  |  | 93°18'40.8" | 26°51'34.4"
[7 empty] | 320 |  |  |  |  | -3.17 | [8 empty] | Tea Garden, Nala, Foot Track
70 |  | 31/8 | DA+0 | 0 | [5 empty] | 87.88 | 0 |  | 626 | 142.0203 | 143.3912 | 285.4115 | 124.984 | 134.2867 | 259.2707 |  |  |  | 93°18'52.3" | 26°51'33.7"
[7 empty] | 306 |  |  |  |  | 1.62 | [8 empty] | Nala, Foot Track, Tea Garden
71 |  | 31/9 | DA+3 | 3 | [5 empty] | 86.5 | 0 |  | 617 | 162.6088 | 167.172 | 329.7807 | 171.7133 | 178.2314 | 349.9448 |  |  |  | 93°19'3.4" | 26°51'33"
[7 empty] | 311 |  |  |  |  | -2 | [8 empty] | Tea Garden, 2Nos Nala, Foot Track
72 | 32 | 32/0 | DB+0 | 0 |  | 11°01'09"LT |  | 3072 | 19601 | 87.5 | 0 |  | 661 | 143.828 | 188.8458 | 332.6738 | 132.7686 | 201.965 | 334.7336 |  |  | VILL-SEHERLIA KUHIAR BARI | 93°19'14.6" | 26°51'32.3"
[7 empty] | 350 |  |  |  |  | -2.67 | [8 empty] | Tea Garden, Nala, Pond, Korang River, Vill Road, LT Line
73 |  | 32/1 | DA+0 | 0 | [5 empty] | 84.83 | 0 |  | 350 | 161.1542 | 157.3687 | 318.5229 | 148.035 | 140.6625 | 288.6975 |  |  |  | 93°19'27.2" | 26°51'33.8"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN ( M ) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN ( HOT) |  |  | WEIGHT SPAN IN ( COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
73 |  | 32/1 | DA+0 | 0 | [5 empty] | 84.83 | 0 |  | 700 | 161.1542 | 157.3687 | 318.5229 | 148.035 | 140.6625 | 288.6975 |  |  |  | 93°19'27.2" | 26°51'33.8"
[7 empty] | 350 |  |  |  |  | 3.4 | [8 empty] | 3 Nos Tea Garden, Hut, Shed, U/C House, 11Kv, Un-Metal Road
74 | 33 | 33/0 | DD+3 | 3 |  | 50°22'08"LT |  | 700 | 20301 | 85.23 | 0 |  | 695 | 192.6313 | 197.9624 | 390.5938 | 209.3375 | 222.0888 | 431.4263 |  |  | VILL-HATIMARA | 93°19'39.8" | 26°51'35.2"
[7 empty] | 345 |  |  |  |  | -4.84 | [8 empty] | 2 Nos Tea Garden
75 |  | 33/1 | DA+0 | 0 | [5 empty] | 83.39 | 0 |  | 670 | 147.0376 | 163.3935 | 310.4311 | 122.9112 | 164.2402 | 287.1514 |  |  |  | 93°19'46.5" | 26°51'44.6"
[7 empty] | 325 |  |  |  |  | -0.16 | [8 empty] | 2 Nos Nala, Tea Garden
76 |  | 33/2 | DA+0 | 0 | [5 empty] | 83.23 | 0 |  | 640 | 161.6065 | 154.9648 | 316.5712 | 160.7598 | 152.5626 | 313.3224 |  |  |  | 93°19'52.9" | 26°51'53.5"
[7 empty] | 315 |  |  |  |  | 0.44
77 |  | 33/3 | DA+0 | 0 | [5 empty] | 83.67 | 0 |  | 627 | 160.0352 | 149.1356 | 309.1708 | 162.4374 | 142.6314 | 305.0689 |  |  |  | 93°19'59" | 26°52'2.2"
[7 empty] | 312 |  |  |  |  | 1.18
78 | 34 | 34/0 | DD+0 | 0 |  | 54°55'37"RT |  | 1297 | 21598 | 84.85 | 0 |  | 642 | 162.8644 | 162.8 | 325.6644 | 169.3686 | 160.7155 | 330.084 |  |  | VILL-HATIMARA | 93°20'5.1" | 26°52'10.7"
[7 empty] | 330 |  |  |  |  | 0.4 | [8 empty] | 2 Nos Tea Garden, Foot Track, Hut, Nala
79 |  | 34/1 | DA+3 | 3 | [5 empty] | 82.25 | 0 |  | 665 | 167.2 | 155.5265 | 322.7265 | 169.2845 | 144.1813 | 313.4658 |  |  |  | 93°20'17" | 26°52'11.2"
[7 empty] | 335 |  |  |  |  | 2.21 | [8 empty] | Tea Garden, Vill Road, 11Kv
80 |  | 34/2 | DA+3 | 3 | [5 empty] | 84.46 | 0 |  | 685 | 179.4735 | 190.6089 | 370.0824 | 190.8187 | 205.3988 | 396.2175 |  |  |  | 93°20'29.2" | 26°52'11.7"
[7 empty] | 350 |  |  |  |  | -3.01
81 |  | 34/3 | DA+0 | 0 | [5 empty] | 84.45 | 0 |  | 700 | 159.3911 | 159.2874 | 318.6785 | 144.6012 | 144.3993 | 289.0005 |  |  |  | 93°20'41.9" | 26°52'12.2"
[7 empty] | 350 |  |  |  |  | 3.03
82 |  | 34/4 | DA+3 | 3 | [5 empty] | 84.48 | 0 |  | 700 | 190.7126 | 175.2593 | 365.9719 | 205.6007 | 175.505 | 381.1057 |  |  |  | 93°20'54.5" | 26°52'12.7"
[7 empty] | 350 |  |  |  |  | -0.05 | [8 empty] | Foot Track, Tea Garden
83 |  | 34/5 | DA+3 | 3 | [5 empty] | 84.43 | 0 |  | 666 | 174.7407 | 174.8288 | 349.5696 | 174.495 | 190.7746 | 365.2697 |  |  |  | 93°21'7.2" | 26°52'13.2"
[7 empty] | 316 |  |  |  |  | -2.93 | [8 empty] | Tea Garden, 2Nos Hut, Vill Road, Pond
84 | 35 | 35/0 | DD+0 | 0 |  | 43°33'44"LT |  | 2031 | 23629 | 84.5 | 0 |  | 654 | 141.1712 | 153.1591 | 294.3303 | 125.2254 | 138.1495 | 263.3748 |  |  | VILL-SIALMARI | 93°21'18.6" | 26°52'13.7"
[7 empty] | 338 |  |  |  |  | 2.95 | [8 empty] | Tea Garden
85 |  | 35/1 | DA+3 | 3 | [5 empty] | 84.45 | 0 |  | 658 | 184.8409 | 176.7319 | 361.5728 | 199.8505 | 192.5859 | 392.4364 |  |  |  | 93°21'27.1" | 26°52'21.6"
[7 empty] | 320 |  |  |  |  | -2.95 | [8 empty] | Vill Road
86 | 36 | 36/0 | DB+0 | 0 |  | 00°42'57"LT |  | 658 | 24287 | 84.5 | 0 |  | 565 | 143.2681 | 124.5002 | 267.7683 | 127.4141 | 126.3954 | 253.8096 |  |  | VILL-KULAGURI JARANI | 93°21'35.1" | 26°52'29.1"
[7 empty] | 245 |  |  |  |  | -0.27 | [8 empty] | Vill Road
87 | 37 | 37/0 | DD+0 | 0 |  | 42°46'11"RT |  | 245 | 24532 | 84.23 | 0 |  | 445 | 120.4998 | 99.7278 | 220.2276 | 118.6046 | 99.4698 | 218.0744 |  |  | VILL-KULAGURI JARANI | 93°21'41.2" | 26°52'34.9"
[7 empty] | 200 |  |  |  |  | 0.03 | [8 empty] | 11Kv, LT Line, Nala, Foot Track
88 | 38 | 38/0 | DD+0 | 0 |  | 52°31'35"LT |  | 200 | 24732 | 84.26 | 0 |  | 530 | 100.2722 | 148.6651 | 248.9374 | 100.5302 | 133.1874 | 233.7176 |  |  | VILL-KULAGURI JARANI | 93°21'48.4" | 26°52'35.3"
[7 empty] | 330 |  |  |  |  | 2.97
89 | 39 | 39/0 | DD+3 | 3 |  | 45°27'56"RT |  | 330 | 25062 | 84.23 | 0 |  | 678 | 181.3349 | 189.6465 | 370.9813 | 196.8126 | 204.4719 | 401.2845 |  |  | VILL-BIHMARI JARANI | 93°21'55" | 26°52'44.3"
[7 empty] | 348 |  |  |  |  | -3 | [8 empty] | Tea Garden, FP, Nala, Pond
90 | 40 | 40/0 | DB+0 | 0 |  | 12°03'06"RT |  | 348 | 25410 | 84.23 | 0 |  | 578 | 158.3535 | 116.1837 | 274.5372 | 143.5281 | 117.3053 | 260.8334 |  |  | VILL-BIHMARI JARANI | 93°22'7.4" | 26°52'46.5"
[7 empty] | 230 |  |  |  |  | -0.15 | [8 empty] | Foot Path, LT Line
91 |  | 40/1 | DA+0 | 0 | [5 empty] | 84.08 | 0 |  | 444 | 113.8163 | 106.6607 | 220.4771 | 112.6947 | 106.3393 | 219.034 |  |  |  | 93°22'15.7" | 26°52'46.3"
[7 empty] | 214 |  |  |  |  | 0.04 | [8 empty] | Metal Road, LT Line, Tea Garden
92 | 41 | 41/0 | DD+0 | 0 |  | 57°25'33"LT |  | 444 | 25854 | 84.12 | 0 |  | 230 | 113.8163 | 157.4326 | 271.2489 | 112.6947 | 152.1572 | 264.852 |  |  | VILL-BIHMARI JARANI | 93°22'23.5" | 26°52'46.2"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN (M) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN (HOT) |  |  | WEIGHT SPAN IN (COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
92 | 41 | 41/0 | DD+0 | 0 |  | 57°25'33"LT |  |  |  | 84.12 | 0 |  | 556 | 113.8163 | 157.4326 | 271.2489 | 112.6947 | 152.1572 | 264.852 |  |  | BIHMARI JARANI | 93°22'23.5" | 26°52'46.2"
[7 empty] | 326 |  |  |  |  | 1 | [8 empty] | 3 Nos Tea Garden, Drain
93 | 42 | 42/0 | DC+0 | 0 |  | 24°53'36"LT |  | 326 | 26180 | 85.12 | 0 |  | 550 | 168.5674 | 111.1087 | 279.6762 | 173.8428 | 110.2642 | 284.1069 |  |  | BIHMARI JARANI | 93°22'30" | 26°52'55"
[7 empty] | 224 |  |  |  |  | 0.11 | [8 empty] | Tea Garden, Pond, Vill Road, LT Line, 11Kv
94 | 43 | 43/0 | DC+0 | 0 |  | 21°48'44"RT |  | 224 | 26404 | 85.23 | 0 |  | 474 | 112.8913 | 125.363 | 238.2543 | 113.7358 | 125.7069 | 239.4428 |  |  | BIHMARI JARANI | 93°22'31.2" | 26°53'2.3"
[7 empty] | 250 |  |  |  |  | -0.05 | [8 empty] | Drain, 11Kv
95 |  | 43/1 | DA+0 | 0 | [5 empty] | 85.18 | 0 |  | 595 | 124.637 | 156.0336 | 280.6706 | 124.2931 | 140.4312 | 264.7243 |  |  |  | 93°22'35.8" | 26°53'9.3"
[7 empty] | 345 |  |  |  |  | 3.13
96 |  | 43/2 | DA+3 | 3 | [5 empty] | 85.31 | 0 |  | 660 | 188.9664 | 163.8381 | 352.8045 | 204.5688 | 169.8435 | 374.4123 |  |  |  | 93°22'42.2" | 26°53'18.9"
[7 empty] | 315 |  |  |  |  | -1.1 | [8 empty] | 3 Nos 11Kv, Canal
97 |  | 43/3 | DA+3 | 3 | [5 empty] | 84.21 | 0 |  | 548 | 151.1619 | 137.6099 | 288.7719 | 145.1565 | 157.6122 | 302.7687 |  |  |  | 93°22'47.9" | 26°53'27.8"
[7 empty] | 233 |  |  |  |  | -2.71 | [8 empty] | 11Kv, Vill Road, Tea Garden
98 | 44 | 44/0 | DD+0 | 0 |  | 54°51'53"RT |  | 1143 | 27547 | 84.5 | 0 |  | 576 | 95.3901 | 156.7367 | 252.1267 | 75.3878 | 142.748 | 218.1359 |  |  | BIHMARI JARANI | 93°22'52.2" | 26°53'34.3"
[7 empty] | 343 |  |  |  |  | 2.79 | [8 empty] | Nala, Tea Garden
99 |  | 44/1 | DA+3 | 3 | [5 empty] | 84.29 | 0 |  | 683 | 186.2633 | 184.8936 | 371.1569 | 200.252 | 199.0056 | 399.2576 |  |  |  | 93°23'4.6" | 26°53'35.2"
[7 empty] | 340 |  |  |  |  | -2.79 | [8 empty] | Tea Garden
100 | 45 | 45/0 | DB+0 | 0 |  | 01°25'03"LT |  | 683 | 28230 | 84.5 | 0 |  | 690 | 155.1064 | 160.169 | 315.2754 | 140.9944 | 146.1161 | 287.1105 |  |  | BIHMARI JARANI | 93°23'16.9" | 26°53'36.1"
[7 empty] | 350 |  |  |  |  | 2.86 | [8 empty] | FP, LT Line, Metal Road
101 |  | 45/1 | DA+3 | 3 | [5 empty] | 84.36 | 0 |  | 700 | 189.831 | 187.9642 | 377.7952 | 203.8839 | 200.2481 | 404.132 |  |  |  | 93°23'29.5" | 26°53'37.3"
[7 empty] | 350 |  |  |  |  | -2.5 | [8 empty] | Tea Garden
102 |  | 45/2 | DB+0 | 0 | [5 empty] | 84.86 | 0 |  | 689 | 162.0358 | 131.7011 | 293.7369 | 149.7519 | 95.8857 | 245.6376 |  |  |  | 93°23'42.1" | 26°53'38.5"
[7 empty] | 339 |  |  |  |  | 7.06 | [8 empty] | Tea Garden
103 |  | 45/3 | DB+6 | 6 | [5 empty] | 85.92 | 0 |  | 689 | 207.2989 | 121.5356 | 328.8345 | 243.1143 | 70.8767 | 313.991 |  |  |  | 93°23'54.4" | 26°53'39.7"
[7 empty] | 350 |  |  |  |  | 10.31 | [8 empty] | 11Kv, Foot Track, 2 Nos Tea Garden
104 | 46 | 46/0 | DD+18 | 18 |  | 07°28'8"RT |  | 1389 | 29619 | 84.23 | 0 |  | 850 | 228.4644 | 249.0199 | 477.4843 | 279.1233 | 248.0912 | 527.2145 |  |  | MADHUPUR | 93°24'7" | 26°53'40.9"
[7 empty] | 500 |  |  |  |  | 0.27 | [8 empty] | Tea Garden, Foot Track, Low Land
105 |  | 46/1 | DD+18 | 18 |  |  |  | 500 | 30119 | 84.5 | 0 |  | 1050 | 250.9801 | 275 | 525.9801 | 251.9088 | 275 | 526.9088 |  |  |  | 93°24'25.1" | 26°53'40.5"
[7 empty] | 550 |  |  |  |  | 0 | [8 empty] | Boroue River
106 |  | 46/2 | DD+18 | 18 |  |  |  | 550 | 30669 | 84.5 | 0 |  | 1050 | 275 | 258.24 | 533.24 | 275 | 266.0477 | 541.0477 |  |  |  | 93°24'45" | 26°53'40.1"
[7 empty] | 500 |  |  |  |  | -2.27 | [8 empty] | Boroue River, Tea Garden, Foot Track
107 | 47 | 47/0 | DD+18 | 18 |  | 50°03'39"LT |  | 500 | 31169 | 82.23 | 0 |  | 850 | 241.76 | 226.8568 | 468.6168 | 233.9523 | 275.9925 | 509.9448 |  |  | RAKHALKUTHI | 93°25'3.1" | 26°53'39.7"
[7 empty] | 350 |  |  |  |  | -10
108 |  | 47/1 | DB+9 | 9 | [5 empty] | 81.23 | 0 |  | 657 | 123.1432 | 206.9446 | 330.0878 | 74.0075 | 257.5848 | 331.5923 |  |  |  | 93°25'11.5" | 26°53'48.2"
[7 empty] | 307 |  |  |  |  | -9.04
109 |  | 47/2 | DB+0 | 0 | [5 empty] | 81.19 | 0 |  | 613 | 100.0554 | 157.8637 | 257.9191 | 49.4152 | 162.4722 | 211.8874 |  |  |  | 93°25'18.8" | 26°53'55.7"
[7 empty] | 306 |  |  |  |  | -0.82
110 |  | 47/3 | DA+0 | 0 | [5 empty] | 80.37 | 0 |  | 306 | 148.1363 | 108.2135 | 256.3498 | 143.5278 | 101.7832 | 245.311 |  |  |  | 93°25'26.1" | 26°54'3.2"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN (M) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN (HOT) |  |  | WEIGHT SPAN IN (COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
110 |  | 47/3 | DA+0 | 0 | [5 empty] | 80.37 | 0 |  | 536 | 148.1363 | 108.2135 | 256.3498 | 143.5278 | 101.7832 | 245.311 |  |  |  | 93°25'26.1" | 26°54'3.2"
[7 empty] | 230 |  |  |  |  | 0.86 | [8 empty] | Foot Track, 11Kv, Vill Road
111 | 48 | 48/0 | DC+0 | 0 |  | 23°06'51"LT |  | 1193 | 32362 | 81.23 | 0 |  | 542 | 121.7865 | 158.9086 | 280.6951 | 128.2168 | 161.6646 | 289.8815 |  |  | VILL-GOSALA | 93°25'31.6" | 26°54'8.8"
[7 empty] | 312 |  |  |  |  | -0.5
112 |  | 48/1 | DA+0 | 0 | [5 empty] | 80.73 | 0 |  | 624 | 153.0914 | 158.9086 | 312 | 150.3354 | 161.6646 | 312 |  |  |  | 93°25'35.2" | 26°54'18.4"
[7 empty] | 312 |  |  |  |  | -0.5
113 |  | 48/2 | DA+0 | 0 | [5 empty] | 80.23 | 0 |  | 622 | 153.0914 | 155 | 308.0914 | 150.3354 | 155 | 305.3354 |  |  |  | 93°25'38.7" | 26°54'28.1"
[7 empty] | 310 |  |  |  |  | 0 | [8 empty] | Boundary Wall
114 | 49 | 49/0 | DD+0 | 0 |  | 52°08'44"RT |  | 934 | 33296 | 80.23 | 0 |  | 630 | 155 | 142.9845 | 297.9845 | 155 | 126.8618 | 281.8618 |  |  | VILL-GOSALA | 93°25'42.2" | 26°54'37.7"
[7 empty] | 320 |  |  |  |  | 3 | [8 empty] | LT Line, Un-Metal Road, Nala, 11Kv
115 |  | 49/1 | DA+3 | 3 | [5 empty] | 80.23 | 0 |  | 642 | 177.0155 | 166.6366 | 343.6521 | 193.1382 | 171.9774 | 365.1156 |  |  |  | 93°25'53.1" | 26°54'41.2"
[7 empty] | 322 |  |  |  |  | -1 | [8 empty] | Nala, FP, Tea Garden
116 | 50 | 50/0 | DC+0 | 0 |  | 21°26'31"RT |  | 642 | 33938 | 82.23 | 0 |  | 645 | 155.3634 | 155.8808 | 311.2442 | 150.0226 | 150.5565 | 300.5791 |  |  | VILL-GOSALA | 93°26'4.1" | 26°54'44.7"
[7 empty] | 323 |  |  |  |  | 1 | [8 empty] | Tea Garden, 2Nos Pond, FP, LT Line, Vill Road, Hut, Boring
117 | 51 | 51/0 | DC+3 | 3 |  | 29°01'21"LT |  | 323 | 34261 | 80.23 | 0 |  | 620 | 167.1192 | 136.2779 | 303.397 | 172.4435 | 124.697 | 297.1405 |  |  | VILL-HALIBARI | 93°26'15.9" | 26°54'44.3"
[7 empty] | 297 |  |  |  |  | 2 | [8 empty] | 11Kv, Nala, Metal Road, LT Line
118 | 52 | 52/0 | DD+6 | 6 |  | 54°49'53"RT |  | 297 | 34558 | 79.23 | 0 |  | 640 | 160.7221 | 176.7915 | 337.5137 | 172.303 | 181.8054 | 354.1083 |  |  | VILL-HALIBARI | 93°26'25.4" | 26°54'48.8"
[7 empty] | 343 |  |  |  |  | -1 | [8 empty] | 11Kv
119 |  | 52/1 | DA+6 | 6 | [5 empty] | 78.23 | 0 |  | 693 | 166.2085 | 211.2998 | 377.5083 | 161.1946 | 245.6948 | 406.8894 |  |  |  | 93°26'36.5" | 26°54'43.6"
[7 empty] | 350 |  |  |  |  | -7
120 |  | 52/2 | DA+0 | 0 | [5 empty] | 77.23 | 0 |  | 690 | 138.7002 | 137.9708 | 276.671 | 104.3052 | 107.6223 | 211.9275 |  |  |  | 93°26'47.7" | 26°54'38.3"
[7 empty] | 340 |  |  |  |  | 6 | [8 empty] | Foot Track
121 |  | 52/3 | DB+6 | 6 |  |  |  | 1033 | 35591 | 77.23 | 0 |  | 740 | 202.0292 | 145.5504 | 347.5796 | 232.3777 | 93.9578 | 326.3356 |  |  |  | 93°26'58.7" | 26°54'33.2"
[7 empty] | 400 |  |  |  |  | 12
122 | 53 | 53/0 | DD+18 | 18 |  | 38°24'32"RT |  | 400 | 35991 | 77.23 | 0 |  | 597 | 254.4496 | 127.1529 | 381.6025 | 306.0422 | 154.3022 | 460.3444 |  |  | VILL-SINGLIJAN | 93°27'11.5" | 26°54'27.2"
[7 empty] | 197 |  |  |  |  | -3.11 | [8 empty] | 132 Kv U/C D/C Biswanath Chariali - Itanagar T/L.
123 |  | 53/1 | DD+15 | 15 |  |  |  | 197 | 36188 | 77.12 | 0 |  | 667 | 69.8471 | 273.192 | 343.0391 | 42.6978 | 309.3799 | 352.0777 |  |  |  | 93°27'14.4" | 26°54'21.3"
[7 empty] | 470 |  |  |  |  | -9.89 | [8 empty] | 11Kv, Vill Road
124 |  | 53/2 | DB+6 | 6 |  |  |  | 470 | 36658 | 76.23 | 0 |  | 870 | 196.808 | 209.0749 | 405.883 | 160.6201 | 217.6737 | 378.2938 |  |  |  | 93°27'21.3" | 26°54'7.4"
[7 empty] | 400 |  |  |  |  | -2
125 | 54 | 54/0 | DC+3 | 3 |  | 23°051'8"LT |  | 400 | 37058 | 77.23 | 0 |  | 730 | 190.9251 | 169.675 | 360.6 | 182.3263 | 174.1046 | 356.4309 |  |  | VILL-SINGLIJAN | 93°27'27.2" | 26°53'55.5"
[7 empty] | 330 |  |  |  |  | -0.85 | [8 empty] | 2 Nos FP, LT Line, 11Kv
126 |  | 54/1 | DA+3 | 3 | [5 empty] | 76.38 | 0 |  | 667 | 160.325 | 147.765 | 308.09 | 155.8954 | 128.118 | 284.0133 |  |  |  | 93°27'36.1" | 26°53'48.3"
[7 empty] | 337 |  |  |  |  | 3.85
127 | 55 | 55/0 | DD+6 | 6 |  | 32°51'54"LT |  | 667 | 37725 | 77.23 | 0 |  | 687 | 189.235 | 175 | 364.235 | 208.882 | 175 | 383.882 |  |  | VILL-SINGLIJAN | 93°27'45.1" | 26°53'40.9"
[7 empty] | 350 |  |  |  |  | 0 | [8 empty] | LT Line, Vill Road, 11Kv
128 |  | 55/1 | DA+6 | 6 | [5 empty] | 77.23 | 0 |  | 350 | 175 | 206.1141 | 381.1141 | 175 | 235.5955 | 410.5955 |  |  |  | 93°27'57.7" | 26°53'39.1"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN ( M ) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN ( HOT) |  |  | WEIGHT SPAN IN ( COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
128 |  | 55/1 | DA+6 | 6 | [5 empty] | 77.23 | 0 |  | 700 | 175 | 206.1141 | 381.1141 | 175 | 235.5955 | 410.5955 |  |  |  | 93°27'57.7" | 26°53'39.1"
[7 empty] | 350 |  |  |  |  | -6 | [8 empty] | Nala
129 |  | 55/2 | DA+0 | 0 | [5 empty] | 77.23 | 0 |  | 700 | 143.8859 | 159.443 | 303.3289 | 114.4045 | 144.7022 | 259.1067 |  |  |  | 93°28'10.2" | 26°53'37.3"
[7 empty] | 350 |  |  |  |  | 3
130 |  | 55/3 | DA+3 | 3 | [5 empty] | 77.23 | 0 |  | 700 | 190.557 | 175 | 365.557 | 205.2978 | 175 | 380.2978 |  |  |  | 93°28'22.7" | 26°53'35.4"
[7 empty] | 350 |  |  |  |  | 0
131 |  | 55/4 | DA+3 | 3 | [5 empty] | 77.23 | 0 |  | 700 | 175 | 185.3714 | 360.3714 | 175 | 195.1985 | 370.1985 |  |  |  | 93°28'35.3" | 26°53'33.6"
[7 empty] | 350 |  |  |  |  | -2 | [8 empty] | Foot Track, Nala
132 | 56 | 56/0 | DD+0 | 0 |  | 39°52'53"RT |  | 1750 | 39475 | 78.23 | 0 |  | 646 | 164.6286 | 148 | 312.6286 | 154.8015 | 148 | 302.8015 |  |  | SINGLIJAN | 93°28'47.8" | 26°53'31.7"
[7 empty] | 296 |  |  |  |  | 0
133 | 57 | 57/0 | DC+0 | 0 |  | 26°19'39"RT |  | 296 | 39771 | 78.23 | 0 |  | 592 | 148 | 154.1317 | 302.1317 | 148 | 159.9417 | 307.9417 |  |  | SINGLIJAN | 93°28'54.8" | 26°53'24.5"
[7 empty] | 296 |  |  |  |  | -1
134 | 58 | 58/0 | DD+0 | 0 |  | 17°00'12"RT |  | 296 | 40067 | 77.23 | 0 |  | 397 | 141.8683 | 115.1927 | 257.0609 | 136.0583 | 176.4907 | 312.549 |  |  | SINGLIJAN | 93°28'57.5" | 26°53'15.2"
[7 empty] | 101 |  |  |  |  | -3.6
135 |  | 58/1 | Gantry | -3.59 |  |  |  | 101 | 40168 | 77.22 | 0 |  | 161 | -14.1927 | 32.42 | 18.2273 | -75.4907 | 34.713 | -40.7777 |  |  |  | 93°28'57.3" | 26°53'11.9"
[7 empty] | 60 |  |  |  |  | -0.08 | [8 empty] | 400 Kv D/C Ranganadi - Balipara T/L.
136 |  | 58/2 | Gantry | -3.59 |  |  |  | 60 | 40228 | 77.14 | 0 |  | 148 | 27.58 | -31.8995 | -4.3195 | 25.287 | -103.8163 | -78.5293 |  |  |  | 93°28'57.2" | 26°53'9.9"
[7 empty] | 88 |  |  |  |  | 3.68
137 | 59 | 59/0 | DD+0 | 0 |  | 11°44'24"LT |  | 88 | 40316 | 77.23 | 0 |  | 387 | 119.8995 | 155.5702 | 275.4697 | 191.8163 | 161.3219 | 353.1382 |  |  | SINGLIJAN | 93°28'57.1" | 26°53'7.1"
[7 empty] | 299 |  |  |  |  | -1 | [8 empty] | FP
138 | 60 | 60/0 | DC+0 | 0 |  | 15°15'36"LT |  | 299 | 40615 | 76.23 | 0 |  | 624 | 143.4298 | 162.5 | 305.9298 | 137.6781 | 162.5 | 300.1781 |  |  | SINGLIJAN | 93°28'58.8" | 26°52'57.5"
[7 empty] | 325 |  |  |  |  | 0
139 |  | 60/1 | DA+0 | 0 | [5 empty] | 76.23 | 0 |  | 650 | 162.5 | 151.3308 | 313.8308 | 162.5 | 140.7478 | 303.2478 |  |  |  | 93°29'3.7" | 26°52'47.9"
[7 empty] | 325 |  |  |  |  | 2
140 |  | 60/2 | DA+3 | 3 | [5 empty] | 75.23 | 0 |  | 674 | 173.6692 | 143.2968 | 316.9659 | 184.2522 | 113.7309 | 297.9831 |  |  |  | 93°29'8.6" | 26°52'38.3"
[7 empty] | 349 |  |  |  |  | 6 | [8 empty] | LT Line, Un-Metal Road
141 | 61 | 61/0 | DC+9 | 9 |  | 19°47'12"LT |  | 999 | 41614 | 75.23 | 0 |  | 814 | 205.7032 | 232.5 | 438.2032 | 235.2691 | 232.5 | 467.7691 |  |  | TOTON BARI | 93°29'13.8" | 26°52'28"
[7 empty] | 465 |  |  |  |  | 0 | [8 empty] | Nala
142 | 62 | 62/0 | DD+9 | 9 |  | 51°07'54"LT |  | 465 | 42079 | 75.23 | 0 |  | 690 | 232.5 | 185.0995 | 417.5995 | 232.5 | 253.8895 | 486.3895 |  |  | TOTON BARI | 93°29'25.6" | 26°52'17.1"
[7 empty] | 225 |  |  |  |  | -9 | [8 empty] | Metal Road, LT Line, FP, Pond, Toilet
143 | 63 | 63/0 | DC+0 | 0 |  | 15°13'43"LT |  | 225 | 42304 | 75.23 | 0 |  | 534 | 39.9005 | 154.5 | 194.4005 | -28.8895 | 154.5 | 125.6105 |  |  | TOTON BARI | 93°29'33.7" | 26°52'17.8"
[7 empty] | 309 |  |  |  |  | 0 | [8 empty] | Pond
144 | 64 | 64/0 | DD+0 | 0 |  | 42°59'3"RT |  | 309 | 42613 | 75.23 | 0 |  | 579 | 154.5 | 135 | 289.5 | 154.5 | 135 | 289.5 |  |  | TOTON BARI | 93°29'44.2" | 26°52'21.4"
[7 empty] | 270 |  |  |  |  | 0 | [8 empty] | Nala, Metal Road, LT Line, 11Kv
145 |  | 64/1 | DA+0 | 0 | [5 empty] | 75.23 | 0 |  | 586 | 135 | 140.7691 | 275.7691 | 135 | 124.4424 | 259.4424 |  |  |  | 93°29'53.3" | 26°52'18"
[7 empty] | 316 |  |  |  |  | 3
146 | 65 | 65/0 | DC+3 | 3 |  | 24°45'46"RT |  | 586 | 43199 | 75.23 | 0 |  | 316 | 175.2309 | 175.3382 | 350.5691 | 191.5576 | 180.3963 | 371.9539 |  |  | TOTON BARI | 93°30'3.9" | 26°52'14.1"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN ( M ) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN ( HOT) |  |  | WEIGHT SPAN IN ( COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
146 | 65 | 65/0 | DC+3 | 3 |  | 24°45'46"RT |  |  |  | 75.23 | 0 |  | 656 | 175.2309 | 175.3382 | 350.5691 | 191.5576 | 180.3963 | 371.9539 |  |  | VILL-TOTON BARI | 93°30'3.9" | 26°52'14.1"
[7 empty] | 340 |  |  |  |  | -1 | [8 empty] | Vill Road, 11Kv
147 | 66 | 66/0 | DD+3 | 3 |  | 35°57'37"LT |  | 340 | 43539 | 74.23 | 0 |  | 675 | 164.6618 | 156.6642 | 321.326 | 159.6037 | 146.3971 | 306.0008 |  |  | VILL-TOTON BARI | 93°30'12.2" | 26°52'6"
[7 empty] | 335 |  |  |  |  | 2 | [8 empty] | FP, Branbhajan River
148 |  | 66/1 | DA+3 | 3 | [5 empty] | 76.23 | 0 |  | 685 | 178.3358 | 190.557 | 368.8928 | 188.6029 | 205.2978 | 393.9007 |  |  |  | 93°30'24.1" | 26°52'3.9"
[7 empty] | 350 |  |  |  |  | -3 | [8 empty] | Tupungjan River, FP
149 | 67 | 67/0 | DB+0 | 0 |  | 09°09'04"LT |  | 685 | 44224 | 76.23 | 0 |  | 625 | 159.443 | 116.6441 | 276.0871 | 144.7022 | 96.8826 | 241.5849 |  |  | VILL-1 NO JOGI BARI | 93°30'36.6" | 26°52'1.7"
[7 empty] | 275 |  |  |  |  | 3.16 | [8 empty] | Pond, LT Line, Foot Track
150 |  | 67/1 | DA+3 | 3 | [5 empty] | 76.39 | 0 |  | 615 | 158.3559 | 186.8687 | 345.2246 | 178.1174 | 202.8523 | 380.9696 |  |  |  | 93°30'46.5" | 26°52'1.4"
[7 empty] | 340 |  |  |  |  | -3.16
151 |  | 67/2 | DA+0 | 0 | [5 empty] | 76.23 | 0 |  | 649 | 153.1313 | 154.5 | 307.6313 | 137.1477 | 154.5 | 291.6477 |  |  |  | 93°30'58.8" | 26°52'1"
[7 empty] | 309 |  |  |  |  | 0 | [8 empty] | Pond, Tea Garden
152 | 68 | 68/0 | DC+0 | 0 |  | 23°27'16"LT |  | 924 | 45148 | 76.23 | 0 |  | 659 | 154.5 | 154.2573 | 308.7573 | 154.5 | 134.603 | 289.103 |  |  | VILL-ITAPARA | 93°31'10" | 26°52'0.6"
[7 empty] | 350 |  |  |  |  | 4 | [8 empty] | Vill Road, Nala
153 |  | 68/1 | DA+3 | 3 | [5 empty] | 77.23 | 0 |  | 700 | 195.7427 | 164.6286 | 360.3714 | 215.397 | 154.8015 | 370.1985 |  |  |  | 93°31'21.9" | 26°52'4.8"
[7 empty] | 350 |  |  |  |  | 2
154 |  | 68/2 | DA+6 | 6 | [5 empty] | 76.23 | 0 |  | 680 | 185.3714 | 181.4999 | 366.8713 | 195.1985 | 197.134 | 392.3325 |  |  |  | 93°31'33.7" | 26°52'9"
[7 empty] | 330 |  |  |  |  | -3 | [8 empty] | Shop, Little Star, School, House, 11Kv, Vill Road
155 | 69 | 69/0 | DC+3 | 3 |  | 15°12'34"LT |  | 1030 | 46178 | 76.23 | 0 |  | 680 | 148.5001 | 175 | 323.5001 | 132.866 | 175 | 307.866 |  |  | VILL-JALAUK BARI | 93°31'44.8" | 26°52'12.9"
[7 empty] | 350 |  |  |  |  | 0 | [8 empty] | Nala
156 |  | 69/1 | DA+3 | 3 | [5 empty] | 76.23 | 0 |  | 681 | 175 | 143.5666 | 318.5666 | 175 | 122.7841 | 297.7841 |  |  |  | 93°31'55" | 26°52'19.6"
[7 empty] | 331 |  |  |  |  | 4 | [8 empty] | Hut, LT Line, Metal Road, Tea Garden
157 | 70 | 70/0 | DD+6 | 6 |  | 37°24'15"RT |  | 681 | 46859 | 77.23 | 0 |  | 675 | 187.4334 | 193.1045 | 380.5379 | 208.2159 | 213.1016 | 421.3175 |  |  | VILL-JALAUK BARI | 93°32'4.7" | 26°52'26"
[7 empty] | 344 |  |  |  |  | -4 | [8 empty] | Tea Garden,Balijan River, LT Line, FP, Hut, Boring, Pond
158 |  | 70/1 | DA+3 | 3 | [5 empty] | 76.23 | 0 |  | 672 | 150.8955 | 175.067 | 325.9625 | 130.8984 | 185.5533 | 316.4517 |  |  |  | 93°32'17.2" | 26°52'25.7"
[7 empty] | 328 |  |  |  |  | -2
159 | 71 | 71/0 | DD+0 | 0 |  | 44°02'38"RT |  | 672 | 47531 | 77.23 | 0 |  | 678 | 152.933 | 181.2747 | 334.2077 | 142.4467 | 187.2201 | 329.6668 |  |  | VILL-GUPSAR | 93°32'29.1" | 26°52'25.5"
[7 empty] | 350 |  |  |  |  | -1.21
160 |  | 71/1 | DA+3 | 3 | [5 empty] | 73.02 | 0 |  | 651 | 168.7253 | 168.7705 | 337.4958 | 162.7799 | 186.0823 | 348.8622 |  |  |  | 93°32'38" | 26°52'17.4"
[7 empty] | 301 |  |  |  |  | -3.03 | [8 empty] | 11Kv
161 |  | 71/2 | DA+3 | 3 | [5 empty] | 69.99 | 0 |  | 651 | 132.2295 | 194.6537 | 326.8833 | 114.9177 | 213.2762 | 328.1939 |  |  |  | 93°32'45.7" | 26°52'10.5"
[7 empty] | 350 |  |  |  |  | -3.79
162 |  | 71/3 | DA+3 | 3 | [5 empty] | 66.2 | 0 |  | 640 | 155.3463 | 166.5921 | 321.9384 | 136.7238 | 187.0512 | 323.775 |  |  |  | 93°32'54.6" | 26°52'2.4"
[7 empty] | 290 |  |  |  |  | -3.45 | [8 empty] | 11Kv
163 |  | 71/4 | DA+0 | 0 | [5 empty] | 65.75 | 0 |  | 563 | 123.4079 | 121.3419 | 244.7498 | 102.9488 | 106.9791 | 209.9279 |  |  |  | 93°33'2" | 26°51'55.7"
[7 empty] | 273 |  |  |  |  | 2.28
164 |  | 71/5 | DA+0 | 0 | [5 empty] | 68.03 | 0 |  | 273 | 151.6581 | 143.7917 | 295.4498 | 166.0209 | 126.065 | 292.0859 |  |  |  | 93°33'9" | 26°51'49.4"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN ( M ) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN ( HOT) |  |  | WEIGHT SPAN IN ( COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
164 |  | 71/5 | DA+0 | 0 | [5 empty] | 68.03 | 0 |  | 598 | 151.6581 | 143.7917 | 295.4498 | 166.0209 | 126.065 | 292.0859 |  |  |  | 93°33'9" | 26°51'49.4"
[7 empty] | 325 |  |  |  |  | 3.35 | [8 empty] | 11Kv
165 |  | 71/6 | DA+3 | 3 | [5 empty] | 68.38 | 0 |  | 635 | 181.2083 | 179.2974 | 360.5058 | 198.935 | 202.3199 | 401.2549 |  |  |  | 93°33'17.3" | 26°51'41.9"
[7 empty] | 310 |  |  |  |  | -4.15 | [8 empty] | Foot Track
166 | 72 | 72/0 | DD+0 | 0 |  | 46°54'01"LT |  | 2199 | 49730 | 67.23 | 0 |  | 557 | 130.7026 | 116.1519 | 246.8544 | 107.6801 | 109.1893 | 216.8694 |  |  | VILL-GUPSAR | 93°33'25.2" | 26°51'34.8"
[7 empty] | 247 |  |  |  |  | 1 | [8 empty] | 33Kv, 11Kv
167 |  | 72/1 | DA+3 | 3 | [5 empty] | 65.23 | 0 |  | 597 | 130.8481 | 185.3714 | 316.2195 | 137.8107 | 195.1985 | 333.0092 |  |  |  | 93°33'34.1" | 26°51'35"
[7 empty] | 350 |  |  |  |  | -2 | [8 empty] | Metal Road, Hut
168 | 73 | 73/0 | DB+0 | 0 |  | 11°08'46"RT |  | 597 | 50327 | 66.23 | 0 |  | 631 | 164.6286 | 95.2868 | 259.9154 | 154.8015 | 52.446 | 207.2475 |  |  | VILL-BHOLAGURI | 93°33'46.8" | 26°51'35.3"
[7 empty] | 281 |  |  |  |  | 7
169 | 74 | 74/0 | DD+9 | 9 |  | 43°46'50"RT |  | 281 | 50608 | 64.23 | 0 |  | 504 | 185.7132 | 32.959 | 218.6723 | 228.554 | -41.4607 | 187.0933 |  |  | VILL-BHOLAGURI | 93°33'56.8" | 26°51'33.8"
[7 empty] | 223 |  |  |  |  | 9.65 | [8 empty] | Railway Line, Railway Boundary
170 | 75 | 75/0 | DD+18 | 18 |  | 00°00'00" |  | 223 | 50831 | 64.88 | 0 |  | 493 | 190.041 | 187.9035 | 377.9445 | 264.4607 | 238.0311 | 502.4917 |  |  | VILL-BHOLAGURI | 93°34'1.7" | 26°51'28"
[7 empty] | 270 |  |  |  |  | -7.87 | [8 empty] | 11Kv, 33Kv, 132 Kv D/C Biswanath Chariali - Gohpur T/L.
171 | 76 | 76/0 | DD+12 | 12 |  | 00°00'00" |  | 270 | 51101 | 63.01 | 0 |  | 519 | 82.0965 | 215.9054 | 298.0019 | 31.9689 | 302.5145 | 334.4835 |  |  | VILL-BHOLAGURI | 93°34'7.5" | 26°51'21"
[7 empty] | 249 |  |  |  |  | -12.54 | [8 empty] | NH-15, 11Kv
172 | 77 | 77/0 | DD+0 | 0 |  | 35°46'02"LT |  | 249 | 51350 | 62.47 | 0 |  | 538 | 33.0946 | 144.5 | 177.5946 | -53.5145 | 144.5 | 90.9855 |  |  | VILL-BHOLAGURI | 93°34'12.9" | 26°51'14.5"
[7 empty] | 289 |  |  |  |  | 0
173 |  | 77/1 | DA+0 | 0 | [5 empty] | 62.47 | 0 |  | 599 | 144.5 | 137.4356 | 281.9356 | 144.5 | 120.7929 | 265.2929 |  |  |  | 93°34'22.9" | 26°51'11.7"
[7 empty] | 310 |  |  |  |  | 3
174 |  | 77/2 | DA+3 | 3 | [5 empty] | 62.47 | 0 |  | 578 | 172.5644 | 127.2277 | 299.7921 | 189.2071 | 120.8107 | 310.0178 |  |  |  | 93°34'33.6" | 26°51'8.7"
[7 empty] | 268 |  |  |  |  | 1 | [8 empty] | Balijan River, 33Kv, FP
175 |  | 77/3 | DA+3 | 3 | [5 empty] | 63.47 | 0 |  | 563 | 140.7723 | 147.5 | 288.2723 | 147.1893 | 147.5 | 294.6893 |  |  |  | 93°34'42.9" | 26°51'6"
[7 empty] | 295 |  |  |  |  | 0 | [8 empty] | 11Kv
176 | 78 | 78/0 | DD+3 | 3 |  | 30°53'03"LT |  | 1162 | 52512 | 63.47 | 0 |  | 647 | 147.5 | 181.1562 | 328.6562 | 147.5 | 186.0419 | 333.5419 |  |  | VILL-MAGANI KOCHARI | 93°34'53.1" | 26°51'3.2"
[7 empty] | 352 |  |  |  |  | -1 | [8 empty] | Metal Road, LT Line, house, Hut, Pond
177 | 79 | 79/0 | DD+0 | 0 |  | 42°02'04"RT |  | 352 | 52864 | 65.47 | 0 |  | 646 | 170.8438 | 153.1734 | 324.0172 | 165.9581 | 159.0229 | 324.981 |  |  | VILL-MAGANI KOCHARI | 93°35'5.5" | 26°51'5.8"
[7 empty] | 294 |  |  |  |  | -1 | [8 empty] | Vill Road
178 | 80 | 80/0 | DD+0 | 0 |  | 50°22'14"LT |  | 294 | 53158 | 64.47 | 0 |  | 596 | 140.8266 | 144.9901 | 285.8167 | 134.9771 | 139.2956 | 274.2726 |  |  | VILL-MAGANI KOCHARI | 93°35'14.8" | 26°51'1.2"
[7 empty] | 302 |  |  |  |  | 1 | [8 empty] | Foot Track
179 | 81 | 81/0 | DD+0 | 0 |  | 30°13'48"LT |  | 302 | 53460 | 65.47 | 0 |  | 602 | 157.0099 | 142.377 | 299.3869 | 162.7044 | 135.1541 | 297.8585 |  |  | VILL-MAGANI HATIMOTA | 93°35'25" | 26°51'4.8"
[7 empty] | 300 |  |  |  |  | 1.26
180 |  | 81/1 | DA+0 | 0 | [5 empty] | 66.73 | 0 |  | 606 | 157.623 | 144.6961 | 302.3191 | 164.8459 | 136.828 | 301.6739 |  |  |  | 93°35'31.7" | 26°51'12.5"
[7 empty] | 306 |  |  |  |  | 1.4 | [8 empty] | Foot Track
181 |  | 81/2 | DA+0 | 0 | [5 empty] | 68.13 | 0 |  | 612 | 161.3039 | 156.9147 | 318.2185 | 169.172 | 160.6239 | 329.796 |  |  |  | 93°35'38.5" | 26°51'20.4"
[7 empty] | 306 |  |  |  |  | -0.66 | [8 empty] | Drain, FP
182 |  | 81/3 | DA+0 | 0 | [5 empty] | 67.47 | 0 |  | 306 | 149.0853 | 152.5 | 301.5853 | 145.3761 | 152.5 | 297.8761 |  |  |  | 93°35'45.4" | 26°51'28.2"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN ( M ) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN ( HOT) |  |  | WEIGHT SPAN IN ( COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
182 |  | 81/3 | DA+0 | 0 | [5 empty] | 67.47 | 0 |  | 611 | 149.0853 | 152.5 | 301.5853 | 145.3761 | 152.5 | 297.8761 |  |  |  | 93°35'45.4" | 26°51'28.2"
[7 empty] | 305 |  |  |  |  | 0 | [8 empty] | Tea Garden
183 | 82 | 82/0 | DD+0 | 0 |  | 32°33'34"RT |  | 1217 | 54677 | 67.47 | 0 |  | 629 | 152.5 | 139.5927 | 292.0927 | 152.5 | 118.3613 | 270.8613 |  |  | VILL-PRUB BARI | 93°35'52.2" | 26°51'36"
[7 empty] | 324 |  |  |  |  | 4 | [8 empty] | Tea Garden, FP, Nala, Tea Garden Road
184 |  | 82/1 | DA+3 | 3 | [5 empty] | 68.47 | 0 |  | 674 | 184.4073 | 190.557 | 374.9643 | 205.6387 | 205.2978 | 410.9365 |  |  |  | 93°36'3.3" | 26°51'39.5"
[7 empty] | 350 |  |  |  |  | -3 | [8 empty] | 3 Nos Tea Garden Road, Drain, Tea Garden
185 |  | 82/2 | DA+0 | 0 | [5 empty] | 68.47 | 0 |  | 700 | 159.443 | 159.443 | 318.8859 | 144.7022 | 144.7022 | 289.4045 |  |  |  | 93°36'15.2" | 26°51'43.3"
[7 empty] | 350 |  |  |  |  | 3 | [8 empty] | Tea Garden Road, Tea Garden
186 |  | 82/3 | DA+3 | 3 | [5 empty] | 68.47 | 0 |  | 700 | 190.557 | 164.6286 | 355.1857 | 205.2978 | 154.8015 | 360.0993 |  |  |  | 93°36'27.2" | 26°51'47"
[7 empty] | 350 |  |  |  |  | 2 | [8 empty] | Tea Garden, 2 Nos Foot Track, Nala, FP
187 | 83 | 83/0 | DC+6 | 6 |  | 23°00'50"RT |  | 1374 | 56051 | 67.47 | 0 |  | 700 | 185.3714 | 181.2747 | 366.646 | 195.1985 | 187.2201 | 382.4186 |  |  | VILL-PRUB BARI | 93°36'39.2" | 26°51'50.8"
[7 empty] | 350 |  |  |  |  | -1.21 | [8 empty] | 11Kv, Metal Road, Satrang River, FP, LT Line
188 |  | 83/1 | DA+6 | 6 | [5 empty] | 66.26 | 0 |  | 700 | 168.7253 | 199.4764 | 368.2017 | 162.7799 | 222.6685 | 385.4484 |  |  |  | 93°36'51.8" | 26°51'50.1"
[7 empty] | 350 |  |  |  |  | -4.72 | [8 empty] | Tea Garden
189 |  | 83/2 | DA+3 | 3 | [5 empty] | 64.54 | 0 |  | 700 | 150.5236 | 180.5487 | 331.0723 | 127.3315 | 185.8062 | 313.1377 |  |  |  | 93°37'4.5" | 26°51'49.4"
[7 empty] | 350 |  |  |  |  | -1.07 | [8 empty] | Tea Garden, Foot Track, Tea Garden Road
190 |  | 83/3 | DA+3 | 3 | [5 empty] | 63.47 | 0 |  | 700 | 169.4513 | 170.281 | 339.7324 | 164.1938 | 165.8097 | 330.0035 |  |  |  | 93°37'17.1" | 26°51'48.6"
[7 empty] | 350 |  |  |  |  | 0.91 | [8 empty] | Tea Garden, Tea Garden Road
191 |  | 83/4 | DA+3 | 3 | [5 empty] | 64.38 | 0 |  | 696 | 179.719 | 193.5104 | 373.2294 | 184.1903 | 212.9446 | 397.1349 |  |  |  | 93°37'29.8" | 26°51'47.9"
[7 empty] | 346 |  |  |  |  | -3.91 | [8 empty] | Tea Garden, Un-Metal Road, Cable Line, 11Kv
192 | 84 | 84/0 | DD+0 | 0 |  | 33°26'12"LT |  | 1746 | 57797 | 63.47 | 0 |  | 642 | 152.4896 | 129.6048 | 282.0944 | 133.0554 | 112.1749 | 245.2304 |  |  | VILL-DALHOUSHE | 93°37'42.3" | 26°51'47.2"
[7 empty] | 296 |  |  |  |  | 3 | [8 empty] | FP
193 |  | 84/1 | DA+3 | 3 | [5 empty] | 63.47 | 0 |  | 579 | 166.3952 | 141.5 | 307.8952 | 183.8251 | 141.5 | 325.3251 |  |  |  | 93°37'51.6" | 26°51'52"
[7 empty] | 283 |  |  |  |  | 0 | [8 empty] | Shed, Metal Road
194 | 85 | 85/0 | DD+3 | 3 |  | 51°01'20"LT |  | 579 | 58376 | 63.47 | 0 |  | 565 | 141.5 | 134.5639 | 276.0639 | 141.5 | 128.4655 | 269.9655 |  |  | VILL-DALHOUSHE | 93°38'0.5" | 26°51'56.6"
[7 empty] | 282 |  |  |  |  | 1 | [8 empty] | LT Line, Foot Track
195 | 86 | 86/0 | DD+3 | 3 |  | 35°04'00"RT |  | 282 | 58658 | 64.47 | 0 |  | 611 | 147.4361 | 180.0019 | 327.438 | 153.5345 | 194.6903 | 348.2249 |  |  | VILL-MOHANIGAON | 93°38'2.1" | 26°52'5.6"
[7 empty] | 329 |  |  |  |  | -2.81
196 |  | 86/1 | DA+3 | 3 | [5 empty] | 61.66 | 0 |  | 592 | 148.9981 | 132.8112 | 281.8093 | 134.3097 | 134.0536 | 268.3633 |  |  |  | 93°38'10.4" | 26°52'13.2"
[7 empty] | 263 |  |  |  |  | -0.19 | [8 empty] | 11Kv
197 | 87 | 87/0 | DC+0 | 0 |  | 20°22'48"LT |  | 592 | 59250 | 64.47 | 0 |  | 603 | 130.1888 | 127.2944 | 257.4832 | 128.9464 | 86.8297 | 215.7761 |  |  | VILL-MOHANIGAON | 93°38'17.1" | 26°52'19.4"
[7 empty] | 340 |  |  |  |  | 8 | [8 empty] | Nala
198 |  | 87/1 | DA+6 | 6 | [5 empty] | 66.47 | 0 |  | 662 | 212.7056 | 172.2732 | 384.9788 | 253.1703 | 182.9549 | 436.1252 |  |  |  | 93°38'22.1" | 26°52'29.5"
[7 empty] | 322 |  |  |  |  | -2 | [8 empty] | 2 Nos LT Line, Vill Road, Holoang River, FP, 11Kv
199 |  | 87/2 | DA+3 | 3 | [5 empty] | 67.47 | 0 |  | 647 | 149.7268 | 167.4144 | 317.1412 | 139.0451 | 172.071 | 311.1161 |  |  |  | 93°38'26.8" | 26°52'39.1"
[7 empty] | 325 |  |  |  |  | -0.88
200 |  | 87/3 | DA+0 | 0 | [5 empty] | 69.59 | 0 |  | 325 | 157.5856 | 132.6932 | 290.2787 | 152.929 | 121.5059 | 274.4349 |  |  |  | 93°38'31.6" | 26°52'48.7"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN ( M ) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN ( HOT) |  |  | WEIGHT SPAN IN ( COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
200 |  | 87/3 | DA+0 | 0 | [5 empty] | 69.59 | 0 |  | 614 | 157.5856 | 132.6932 | 290.2787 | 152.929 | 121.5059 | 274.4349 |  |  |  | 93°38'31.6" | 26°52'48.7"
[7 empty] | 289 |  |  |  |  | 1.88
201 | 88 | 88/0 | DD+0 | 0 |  | 38°28'13"RT |  | 1276 | 60526 | 71.47 | 0 |  | 594 | 156.3068 | 140.5984 | 296.9053 | 167.4941 | 129.3214 | 296.8155 |  |  | VILL-BALITIKA | 93°38'35.8" | 26°52'57.3"
[7 empty] | 305 |  |  |  |  | 2 | [8 empty] | Vill Road
202 |  | 88/1 | DA+0 | 0 | [5 empty] | 73.47 | 0 |  | 611 | 164.4016 | 153 | 317.4016 | 175.6786 | 153 | 328.6786 |  |  |  | 93°38'45.6" | 26°53'1.9"
[7 empty] | 306 |  |  |  |  | 0
203 |  | 88/2 | DA+0 | 0 | [5 empty] | 73.47 | 0 |  | 611 | 153 | 152.5 | 305.5 | 153 | 152.5 | 305.5 |  |  |  | 93°38'55.4" | 26°53'6.5"
[7 empty] | 305 |  |  |  |  | 0
204 | 89 | 89/0 | DD+0 | 0 |  | 34°02'17"RT |  | 916 | 61442 | 73.47 | 0 |  | 655 | 152.5 | 154.9833 | 307.4833 | 152.5 | 136.0169 | 288.5169 |  |  | VILL-BALITIKA | 93°39'5.2" | 26°53'11.1"
[7 empty] | 350 |  |  |  |  | 3.86 | [8 empty] | FP, Nala
205 |  | 89/1 | DA+3 | 3 | [5 empty] | 74.33 | 0 |  | 700 | 195.0167 | 185.8381 | 380.8548 | 213.9831 | 196.1074 | 410.0906 |  |  |  | 93°39'17.8" | 26°53'9.9"
[7 empty] | 350 |  |  |  |  | -2.09
206 |  | 89/2 | DA+0 | 0 | [5 empty] | 75.24 | 0 |  | 685 | 164.1619 | 155.4181 | 319.5801 | 153.8926 | 143.9702 | 297.8628 |  |  |  | 93°39'30.4" | 26°53'8.6"
[7 empty] | 335 |  |  |  |  | 2.23 | [8 empty] | House, Vill Road, Pond
207 | 91 | 91/0 | DD+0 | 0 |  | 50°18'42"LT |  | 1035 | 62477 | 77.47 | 0 |  | 660 | 179.5819 | 164.9014 | 344.4832 | 191.0298 | 167.1767 | 358.2065 |  |  | VILL-KAMALA PATHOR | 93°39'42.5" | 26°53'7.4"
[7 empty] | 325 |  |  |  |  | -0.43
208 |  | 91/1 | DA+0 | 0 | [5 empty] | 77.04 | 0 |  | 651 | 160.0986 | 166.1734 | 326.2721 | 157.8233 | 169.1804 | 327.0036 |  |  |  | 93°39'51" | 26°53'14.7"
[7 empty] | 326 |  |  |  |  | -0.57
209 |  | 91/2 | DA+0 | 0 | [5 empty] | 76.47 | 0 |  | 676 | 159.8266 | 159.443 | 319.2695 | 156.8196 | 144.7022 | 301.5219 |  |  |  | 93°39'59.5" | 26°53'22"
[7 empty] | 350 |  |  |  |  | 3
210 |  | 91/3 | DA+3 | 3 | [5 empty] | 76.47 | 0 |  | 631 | 190.557 | 166.3361 | 356.8932 | 205.2978 | 190.8166 | 396.1143 |  |  |  | 93°40'8.7" | 26°53'29.9"
[7 empty] | 281 |  |  |  |  | -4 | [8 empty] | 11Kv
211 | 92 | 92/0 | DD+0 | 0 |  | 30°16'02"RT |  | 1282 | 63759 | 75.47 | 0 |  | 631 | 114.6639 | 143.8859 | 258.5498 | 90.1834 | 114.4045 | 204.5879 |  |  | VILL-KOLIKA CHARIALI | 93°40'16" | 26°53'36.3"
[7 empty] | 350 |  |  |  |  | 6 | [8 empty] | 2 Nos Pond, Metal Road
212 |  | 92/1 | DA+6 | 6 | [5 empty] | 75.47 | 0 |  | 700 | 206.1141 | 188.0161 | 394.1301 | 235.5955 | 200.3491 | 435.9446 |  |  |  | 93°40'28.3" | 26°53'39.1"
[7 empty] | 350 |  |  |  |  | -2.51 | [8 empty] | 11Kv
213 |  | 92/2 | DA+3 | 3 | [5 empty] | 75.96 | 0 |  | 700 | 161.9839 | 190.4015 | 352.3854 | 149.6509 | 204.9948 | 354.6457 |  |  |  | 93°40'40.6" | 26°53'41.8"
[7 empty] | 350 |  |  |  |  | -2.97 | [8 empty] | FP, Kokila River
214 |  | 92/3 | DA+0 | 0 | [5 empty] | 75.99 | 0 |  | 689 | 159.5985 | 172.2841 | 331.8826 | 145.0052 | 174.922 | 319.9272 |  |  |  | 93°40'52.9" | 26°53'44.6"
[7 empty] | 339 |  |  |  |  | -0.52
215 |  | 92/4 | DA+0 | 0 | [5 empty] | 75.47 | 0 |  | 689 | 166.7159 | 155.2944 | 322.0104 | 164.078 | 136.6228 | 300.7008 |  |  |  | 93°41'4.8" | 26°53'47.3"
[7 empty] | 350 |  |  |  |  | 3.8
216 |  | 92/5 | DA+3 | 3 | [5 empty] | 76.27 | 0 |  | 700 | 194.7056 | 194.7056 | 389.4112 | 213.3772 | 213.3772 | 426.7543 |  |  |  | 93°41'17.1" | 26°53'50.1"
[7 empty] | 350 |  |  |  |  | -3.8 | [8 empty] | Vill Road
217 | 93 | 93/0 | DC+0 | 0 |  | 17°18'22"RT |  | 2089 | 65848 | 75.47 | 0 |  | 690 | 155.2944 | 164.6618 | 319.9562 | 136.6228 | 159.6037 | 296.2265 |  |  | VILL-1 NO KOLIKA GURI | 93°41'29.4" | 26°53'52.9"
[7 empty] | 340 |  |  |  |  | 1 | [8 empty] | FP, Dubia River, 11Kv
218 |  | 93/1 | DA+3 | 3 | [5 empty] | 73.47 | 0 |  | 340 | 175.3382 | 167.172 | 342.5102 | 180.3963 | 178.2314 | 358.6277 |  |  |  | 93°41'41.7" | 26°53'52.2"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN ( M ) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN ( HOT) |  |  | WEIGHT SPAN IN ( COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
218 |  | 93/1 | DA+3 | 3 | [5 empty] | 73.47 | 0 |  | 651 | 175.3382 | 167.172 | 342.5102 | 180.3963 | 178.2314 | 358.6277 |  |  |  | 93°41'41.7" | 26°53'52.2"
[7 empty] | 311 |  |  |  |  | -2 | [8 empty] | 2 Nos FP, 11Kv
219 |  | 93/2 | DA+0 | 0 | [5 empty] | 74.47 | 0 |  | 661 | 143.828 | 164.6286 | 308.4567 | 132.7686 | 154.8015 | 287.5701 |  |  |  | 93°41'53" | 26°53'51.7"
[7 empty] | 350 |  |  |  |  | 2 | [8 empty] | 2 Nos Fishery
220 |  | 93/3 | DA+3 | 3 | [5 empty] | 73.47 | 0 |  | 700 | 185.3714 | 175 | 360.3714 | 195.1985 | 175 | 370.1985 |  |  |  | 93°42'5.7" | 26°53'51.1"
[7 empty] | 350 |  |  |  |  | 0
221 |  | 93/4 | DA+3 | 3 | [5 empty] | 73.47 | 0 |  | 621 | 175 | 155.5921 | 330.5921 | 175 | 174.6299 | 349.6299 |  |  |  | 93°42'18.3" | 26°53'50.4"
[7 empty] | 271 |  |  |  |  | -3 | [8 empty] | Vill Road, LT Line
222 | 94 | 94/0 | DC+0 | 0 |  | 18°01'34"LT |  | 1622 | 67470 | 73.47 | 0 |  | 573 | 115.4079 | 132.9703 | 248.3782 | 96.3701 | 115.8867 | 212.2568 |  |  | VILL-KUMAR KATA | 93°42'28.1" | 26°53'49.9"
[7 empty] | 302 |  |  |  |  | 3
223 |  | 94/1 | DA+3 | 3 | [5 empty] | 73.47 | 0 |  | 563 | 169.0297 | 123.546 | 292.5757 | 186.1133 | 116.9569 | 303.0702 |  |  |  | 93°42'38.7" | 26°53'52.4"
[7 empty] | 261 |  |  |  |  | 1 | [8 empty] | 11Kv
224 | 95 | 95/0 | DD+3 | 3 |  | 31°15'56"RT |  | 563 | 68033 | 74.47 | 0 |  | 572 | 137.454 | 108.8122 | 246.2662 | 144.0431 | 64.5743 | 208.6173 |  |  | VILL-2 NO KUMAR KATA | 93°42'47.9" | 26°53'54.6"
[7 empty] | 311 |  |  |  |  | 8 | [8 empty] | Vill Road, LT Line, 2Nos Pond, Changmara River
225 | 96 | 96/0 | DD+9 | 9 |  | 49°03'17"RT |  | 311 | 68344 | 76.47 | 0 |  | 787 | 202.1878 | 241.813 | 444.0008 | 246.4257 | 245.4259 | 491.8517 |  |  | VILL-3 NO KUMAR KATA | 93°42'58.7" | 26°53'51.8"
[7 empty] | 476 |  |  |  |  | -1 | [8 empty] | 11Kv
226 | 97 | 97/0 | DD+9 | 9 |  | 46°18'16"LT |  | 476 | 68820 | 75.47 | 0 |  | 779 | 234.187 | 199.4205 | 433.6075 | 230.5741 | 244.8264 | 475.4005 |  |  | VILL-CHANGMARA | 93°43'5.8" | 26°53'37.7"
[7 empty] | 303 |  |  |  |  | -8 | [8 empty] | LT Line ,2 Nos Vill Road, Pond, Foot Track
227 | 98 | 98/0 | DD+0 | 0 |  | 53°58'54"LT |  | 303 | 69123 | 76.47 | 0 |  | 612 | 103.5795 | 159.9626 | 263.5421 | 58.1736 | 165.1385 | 223.3121 |  |  | VILL-CHANGMARA GURI | 93°43'16.2" | 26°53'34.4"
[7 empty] | 309 |  |  |  |  | -0.93 | [8 empty] | Foot Track, LT Line
228 |  | 98/1 | DA+0 | 0 | [5 empty] | 75.54 | 0 |  | 618 | 149.0374 | 154.9112 | 303.9486 | 143.8615 | 155.3007 | 299.1622 |  |  |  | 93°43'25.4" | 26°53'40.2"
[7 empty] | 309 |  |  |  |  | -0.07
229 | 99 | 99/0 | DC+0 | 0 |  | 23°51'58"LT |  | 618 | 69741 | 75.47 | 0 |  | 546 | 154.0888 | 126.1582 | 280.247 | 153.6993 | 133.4145 | 287.1138 |  |  | VILL-CHANGMARA GURI | 93°43'34.6" | 26°53'45.9"
[7 empty] | 237 |  |  |  |  | -1
230 | 100 | 100/0 | DB+0 | 0 |  | 11°57'42"LT |  | 237 | 69978 | 74.47 | 0 |  | 445 | 110.8418 | 95.2741 | 206.1159 | 103.5855 | 87.0061 | 190.5916 |  |  | VILL-CHANGMARA GURI | 93°43'39.1" | 26°53'52.5"
[7 empty] | 208 |  |  |  |  | 1 | [8 empty] | NH-15, 2Nos Pond
231 | 101 | 101/0 | DD+0 | 0 |  | 34°47'10"RT |  | 208 | 70186 | 75.47 | 0 |  | 503 | 112.7259 | 104.4325 | 217.1584 | 120.9939 | 63.6248 | 184.6188 |  |  | VILL-CHANGMARA GURI | 93°43'41.6" | 26°53'58.9"
[7 empty] | 295 |  |  |  |  | 7 | [8 empty] | Un- Metal Road, 2Nos 11Kv
232 | 102 | 102/0 | DC+6 | 6 |  | 18°18'05"RT |  | 295 | 70481 | 76.47 | 0 |  | 595 | 190.5675 | 162.0999 | 352.6674 | 231.3752 | 173.5649 | 404.9401 |  |  | VILL-CHANGMARA GURI | 93°43'50.3" | 26°54'4.5"
[7 empty] | 300 |  |  |  |  | -2 | [8 empty] | Pond, Shed, 11Kv
233 |  | 102/1 | DA+3 | 3 | [5 empty] | 77.47 | 0 |  | 650 | 137.9001 | 175 | 312.9001 | 126.4351 | 175 | 301.4351 |  |  |  | 93°44'0.6" | 26°54'7.4"
[7 empty] | 350 |  |  |  |  | 0
234 |  | 102/2 | DA+3 | 3 | [5 empty] | 77.47 | 0 |  | 690 | 175 | 153.9854 | 328.9854 | 175 | 138.8111 | 313.8111 |  |  |  | 93°44'12.7" | 26°54'10.9"
[7 empty] | 340 |  |  |  |  | 3 | [8 empty] | LT Line, Un-Metal Road
235 |  | 102/3 | DA+6 | 6 | [5 empty] | 77.47 | 0 |  | 690 | 186.0146 | 206.1141 | 392.1287 | 201.1889 | 235.5955 | 436.7844 |  |  |  | 93°44'24.5" | 26°54'14.2"
[7 empty] | 350 |  |  |  |  | -6
236 |  | 102/4 | DA+0 | 0 | [5 empty] | 77.47 | 0 |  | 350 | 143.8859 | 155.5018 | 299.3878 | 114.4045 | 137.0268 | 251.4313 |  |  |  | 93°44'36.6" | 26°54'17.6"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN (M) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN (HOT) |  |  | WEIGHT SPAN IN (COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
236 |  | 102/4 | DA+0 | 0 | [5 empty] | 77.47 | 0 |  | 700 | 143.8859 | 155.5018 | 299.3878 | 114.4045 | 137.0268 | 251.4313 |  |  |  | 93°44'36.6" | 26°54'17.6"
[7 empty] | 350 |  |  |  |  | 3.76 | [8 empty] | Pond
237 |  | 102/5 | DA+3 | 3 | [5 empty] | 78.23 | 0 |  | 699 | 194.4982 | 194.054 | 388.5522 | 212.9732 | 212.582 | 425.5552 |  |  |  | 93°44'48.7" | 26°54'21"
[7 empty] | 349 |  |  |  |  | -3.76 | [8 empty] | Pond
238 |  | 102/6 | DA+0 | 0 | [5 empty] | 77.47 | 0 |  | 688 | 154.946 | 153.4382 | 308.3841 | 136.418 | 138.2191 | 274.6371 |  |  |  | 93°45'0.8" | 26°54'24.5"
[7 empty] | 339 |  |  |  |  | 3
239 |  | 102/7 | DA+3 | 3 | [5 empty] | 77.47 | 0 |  | 682 | 185.5618 | 171.5 | 357.0618 | 200.7809 | 171.5 | 372.2809 |  |  |  | 93°45'12.5" | 26°54'27.8"
[7 empty] | 343 |  |  |  |  | 0 | [8 empty] | Pond
240 | 103 | 103/0 | DD+3 | 3 |  | 36°41'29"RT |  | 2721 | 73202 | 77.47 | 0 |  | 673 | 171.5 | 181.4999 | 352.9999 | 171.5 | 197.134 | 368.634 |  |  | MAJOR DOLANI | 93°45'24.3" | 26°54'31.1"
[7 empty] | 330 |  |  |  |  | -3 | [8 empty] | FP, Nala
241 |  | 103/1 | DA+0 | 0 | [5 empty] | 77.47 | 0 |  | 680 | 148.5001 | 159.443 | 307.9431 | 132.866 | 144.7022 | 277.5683 |  |  |  | 93°45'35.6" | 26°54'27.6"
[7 empty] | 350 |  |  |  |  | 3
242 |  | 103/2 | DA+3 | 3 | [5 empty] | 77.47 | 0 |  | 700 | 190.557 | 195.7427 | 386.2998 | 205.2978 | 215.397 | 420.6948 |  |  |  | 93°45'47.6" | 26°54'23.9"
[7 empty] | 350 |  |  |  |  | -4
243 | 104 | 104/0 | DD+0 | 0 |  | 32°24'25"LT |  | 1030 | 74232 | 76.47 | 0 |  | 695 | 154.2573 | 153.9293 | 308.1865 | 134.603 | 136.333 | 270.936 |  |  | KHALIHAMARI | 93°45'59.6" | 26°54'20.2"
[7 empty] | 345 |  |  |  |  | 3.53 | [8 empty] | 2 Nos Pond, 11Kv, Un-Metal Road
244 |  | 104/1 | DA+3 | 3 | [5 empty] | 77 | 0 |  | 677 | 191.0707 | 185.2979 | 376.3687 | 208.667 | 203.5832 | 412.2502 |  |  |  | 93°46'11.7" | 26°54'22.7"
[7 empty] | 332 |  |  |  |  | -3.53 | [8 empty] | FP
245 | 105 | 105/0 | DC+0 | 0 |  | 25°28'49"LT |  | 677 | 74909 | 76.47 | 0 |  | 619 | 146.7021 | 142.4249 | 289.127 | 128.4168 | 141.4063 | 269.823 |  |  | KHALIHAMARI | 93°46'23.5" | 26°54'25.2"
[7 empty] | 287 |  |  |  |  | 0.17 | [8 empty] | FP, Pond
246 |  | 105/1 | DA+0 | 0 | [5 empty] | 76.64 | 0 |  | 575 | 144.5751 | 138.7693 | 283.3444 | 145.5937 | 133.8131 | 279.4068 |  |  |  | 93°46'31.6" | 26°54'31"
[7 empty] | 288 |  |  |  |  | 0.83
247 | 106 | 106/0 | DB+0 | 0 |  | 00°54'27"RT |  | 575 | 75484 | 77.47 | 0 |  | 596 | 149.2307 | 118.6431 | 267.8738 | 154.1869 | 85.1415 | 239.3284 |  |  | 1 NO KHALIHAMARI | 93°46'39.7" | 26°54'36.9"
[7 empty] | 308 |  |  |  |  | 6 | [8 empty] | Hut, LT Line, Vill Road
248 |  | 106/1 | DA+6 | 6 | [5 empty] | 77.47 | 0 |  | 658 | 189.3569 | 143.8859 | 333.2428 | 222.8585 | 114.4045 | 337.263 |  |  |  | 93°46'48.5" | 26°54'43"
[7 empty] | 350 |  |  |  |  | 6
249 | 107 | 107/0 | DD+12 | 12 |  | 37°32'24"LT |  | 658 | 76142 | 77.47 | 0 |  | 536 | 206.1141 | 91.2436 | 297.3576 | 235.5955 | 89.5793 | 325.1748 |  |  | 2 NO KHALIHAMARI | 93°46'58.6" | 26°54'50"
[7 empty] | 186 |  |  |  |  | 0.18 | [8 empty] | 132 KV D/C T/L.
250 |  | 107/1 | DD+12 | 12 |  |  |  | 186 | 76328 | 77.65 | 0 |  | 536 | 94.7564 | 204.0917 | 298.8481 | 96.4207 | 231.6568 | 328.0775 |  |  |  | 93°47'0.3" | 26°54'55.8"
[7 empty] | 350 |  |  |  |  | -5.61 | [8 empty] | 2 Nos FP, Pechola River
251 |  | 107/2 | DA+6 | 6 | [5 empty] | 78.04 | 0 |  | 700 | 145.9083 | 209.0699 | 354.9783 | 118.3432 | 241.3521 | 359.6953 |  |  |  | 93°47'3.5" | 26°55'6.8"
[7 empty] | 350 |  |  |  |  | -6.57 | [8 empty] | FP, Pechola River
252 | 107A | 107A/0 | DB+0 | 0 |  | 5°18'51"RT |  | 700 | 77028 | 77.47 | 0 |  | 660 | 140.9301 | 137.4356 | 278.3657 | 108.6479 | 120.7929 | 229.4408 |  |  | 2 NO KHALIHAMARI | 93°47'6.7" | 26°55'17.9"
[7 empty] | 310 |  |  |  |  | 3 | [8 empty] | Pond, Pechola River
253 |  | 107A/1 | DA+3 | 3 | [5 empty] | 77.47 | 0 |  | 629 | 172.5644 | 142.4311 | 314.9955 | 189.2071 | 126.2579 | 315.4651 |  |  |  | 93°47'10.5" | 26°55'27.3"
[7 empty] | 319 |  |  |  |  | 3 | [8 empty] | 11Kv, Metal Road
254 | 108 | 108/0 | DD+6 | 6 |  | 54°30'36"RT |  | 629 | 77657 | 77.47 | 0 |  | 319 | 176.5689 | 196.0075 | 372.5763 | 192.7421 | 227.7567 | 420.4988 |  |  | PETWA GUSANI THAN | 93°47'14.5" | 26°55'37.1"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN (M) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN (HOT) |  |  | WEIGHT SPAN IN (COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
254 | 108 | 108/0 | DD+6 | 6 |  | 54°30'36"RT |  |  |  | 77.47 | 0 |  | 644 | 176.5689 | 196.0075 | 372.5763 | 192.7421 | 227.7567 | 420.4988 |  |  | PETWA GUSANI THAN | 93°47'14.5" | 26°55'37.1"
[7 empty] | 325 |  |  |  |  | -6 | [8 empty] | Metal Road, Pechola River
255 | 109 | 109/0 | DC+0 | 0 |  | 22°14'48"RT |  | 325 | 77982 | 77.47 | 0 |  | 645 | 128.9925 | 160 | 288.9925 | 97.2433 | 160 | 257.2433 |  |  | PETWA GUSANI THAN | 93°47'25.9" | 26°55'39.9"
[7 empty] | 320 |  |  |  |  | 0
256 |  | 109/1 | DA+0 | 0 | [5 empty] | 77.47 | 0 |  | 640 | 160 | 160 | 320 | 160 | 160 | 320 |  |  |  | 93°47'37.4" | 26°55'38.7"
[7 empty] | 320 |  |  |  |  | 0
257 |  | 109/2 | DA+0 | 0 | [5 empty] | 77.47 | 0 |  | 617 | 160 | 142.3889 | 302.3889 | 160 | 136.5985 | 296.5985 |  |  |  | 93°47'48.9" | 26°55'37.5"
[7 empty] | 297 |  |  |  |  | 1 | [8 empty] | Pond, Metal Road, LT Line
258 | 110 | 110/0 | DD+3 | 3 |  | 54°41'55"LT |  | 937 | 78919 | 75.47 | 0 |  | 638 | 154.6111 | 165.1775 | 319.7885 | 160.4015 | 160.1342 | 320.5357 |  |  | DHALPUR | 93°47'59.6" | 26°55'36.3"
[7 empty] | 341 |  |  |  |  | 1
259 | 111 | 111/0 | DC+3 | 3 |  | 28°8'22"LT |  | 341 | 79260 | 76.47 | 0 |  | 674 | 175.8225 | 161.0496 | 336.8721 | 180.8658 | 155.8852 | 336.751 |  |  | DHALPUR | 93°48'7.9" | 26°55'44.6"
[7 empty] | 333 |  |  |  |  | 1
260 | 112 | 112/0 | DC+3 | 3 |  | 15°12'5"LT |  | 333 | 79593 | 77.47 | 0 |  | 548 | 171.9504 | 132.8254 | 304.7758 | 177.1148 | 156.8219 | 333.9368 |  |  | KHANA PICHONA | 93°48'10.8" | 26°55'55.1"
[7 empty] | 215 |  |  |  |  | -3 | [8 empty] | Vill Road, 2Nos LT Line
261 | 113 | 113/0 | DD+0 | 0 |  | 35°1'20"RT |  | 215 | 79808 | 77.47 | 0 |  | 565 | 82.1746 | 169.8143 | 251.9889 | 58.1781 | 164.9007 | 223.0788 |  |  | KHANA PICHONA | 93°48'10.7" | 26°56'2.1"
[7 empty] | 350 |  |  |  |  | 1 | [8 empty] | 3 Nos Pond, Vill Road, LT Line, 11Kv
262 | 114 | 114/0 | DC+3 | 3 |  | 20°24'36"RT |  | 350 | 80158 | 75.47 | 0 |  | 681 | 180.1857 | 170.9833 | 351.169 | 185.0993 | 176.179 | 361.2782 |  |  | KHANA PICHONA | 93°48'17.8" | 26°56'11.5"
[7 empty] | 331 |  |  |  |  | -1 | [8 empty] | Vill Road, Nala, LT Line
263 | 115 | 115/0 | DB+3 | 3 |  | 11°20'3"LT |  | 331 | 80489 | 74.47 | 0 |  | 707 | 160.0167 | 183.1729 | 343.1896 | 154.821 | 178.5991 | 333.4201 |  |  | KHANA PICHONA | 93°48'27.5" | 26°56'17.7"
[7 empty] | 376 |  |  |  |  | 1 | [8 empty] | Pond
264 | 116 | 116/0 | DC+3 | 3 |  | 20°35'14"RT |  | 376 | 80865 | 75.47 | 0 |  | 704 | 192.8271 | 171.1936 | 364.0206 | 197.4009 | 178.0096 | 375.4105 |  |  | KHANA PICHONA | 93°48'36.38" | 26°56'26.62"
[7 empty] | 328 |  |  |  |  | -1.3
265 |  | 116/1 | DA+3 | 3 | [5 empty] | 74.17 | 0 |  | 619 | 156.8064 | 152.9845 | 309.7909 | 149.9904 | 160.0762 | 310.0666 |  |  |  | 93°48'47.5" | 26°56'31.3"
[7 empty] | 291 |  |  |  |  | -1.2 | [8 empty] | 11Kv, Cable Line, LT Line, Metal Road
266 |  | 116/2 | DA+3 | 3 | [5 empty] | 72.97 | 0 |  | 626 | 138.0155 | 186.4626 | 324.4781 | 130.9238 | 204.4301 | 335.3539 |  |  |  | 93°48'57" | 26°56'35.5"
[7 empty] | 335 |  |  |  |  | -3.5 | [8 empty] | FP, Vill Road
267 | 117 | 117/0 | DD+0 | 0 |  | 53°19'29"LT |  | 954 | 81819 | 72.47 | 0 |  | 651 | 148.5374 | 158 | 306.5374 | 130.5699 | 158 | 288.5699 |  |  | KHANA PICHONA | 93°49'7.9" | 26°56'40.3"
[7 empty] | 316 |  |  |  |  | 0
268 |  | 117/1 | DA+0 | 0 | [5 empty] | 72.47 | 0 |  | 656 | 158 | 148.6472 | 306.6472 | 158 | 128.4148 | 286.4148 |  |  |  | 93°49'9.9" | 26°56'50.4"
[7 empty] | 340 |  |  |  |  | 4 | [8 empty] | Pond, Vill Road
269 | 118 | 118/0 | DD+3 | 3 |  | 49°11'45"RT |  | 656 | 82475 | 73.47 | 0 |  | 697 | 191.3528 | 173.416 | 364.7688 | 211.5852 | 168.5988 | 380.1839 |  |  | KHANA PICHONA | 93°49'12" | 26°57'1.3"
[7 empty] | 357 |  |  |  |  | 1 | [8 empty] | Pond
270 | 119 | 119/0 | DB+3 | 3 |  | 11°36'36"RT |  | 357 | 82832 | 74.47 | 0 |  | 707 | 183.584 | 171.7849 | 355.3689 | 188.4012 | 168.7385 | 357.1397 |  |  | SARAI DHOLANI | 93°49'23.1" | 26°57'7.2"
[7 empty] | 350 |  |  |  |  | 0.62 | [8 empty] | 2 Nos Pond, LT Line, Metal Road
271 |  | 119/1 | DA+6 | 6 | [5 empty] | 72.09 | 0 |  | 696 | 178.2151 | 197.2348 | 375.4499 | 181.2615 | 220.198 | 401.4595 |  |  |  | 93°49'35.1" | 26°57'11"
[7 empty] | 346 |  |  |  |  | -4.62 | [8 empty] | LT Line, Cable line, Vill Road, Nala
272 | 120 | 120/0 | DD+0 | 0 |  | 47°35'46"LT |  | 696 | 83528 | 73.47 | 0 |  | 346 | 148.7652 | 145.5007 | 294.2659 | 125.802 | 145.9751 | 271.7771 |  |  | SARAI DHOLANI | 93°49'47" | 26°57'14.7"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN (M) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN (HOT) |  |  | WEIGHT SPAN IN (COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
272 | 120 | 120/0 | DD+0 | 0 |  | 47°35'46"LT |  |  |  | 73.47 | 0 |  | 636 | 148.7652 | 145.5007 | 294.2659 | 125.802 | 145.9751 | 271.7771 |  |  | SARAI DHOLANI | 93°49'47" | 26°57'14.7"
[7 empty] | 290 |  |  |  |  | -0.08 | [8 empty] | FP, Pond
273 |  | 120/1 | DA+0 | 0 | [5 empty] | 73.39 | 0 |  | 635 | 144.4993 | 140.5141 | 285.0134 | 144.0249 | 110.2066 | 254.2315 |  |  |  | 93°49'51.1" | 26°57'23.4"
[7 empty] | 345 |  |  |  |  | 6.08 | [8 empty] | 11Kv, 2Nos Pond
274 | 121 | 121/0 | DD+6 | 6 |  | 49°5'53"LT |  | 635 | 84163 | 73.47 | 0 |  | 677 | 204.4859 | 176.9337 | 381.4195 | 234.7934 | 187.2936 | 422.087 |  |  | SARAI DHOLANI | 93°49'56" | 26°57'33.7"
[7 empty] | 332 |  |  |  |  | -2 | [8 empty] | 2 Nos LT Line, Un-Metal Road, 11Kv
275 | 122 | 122/0 | DD+3 | 3 |  | 7°8'50"LT |  | 332 | 84495 | 74.47 | 0 |  | 447 | 155.0663 | 160.5598 | 315.6261 | 144.7064 | 258.2117 | 402.9181 |  |  | DERGUWA | 93°49'50.8" | 26°57'43.4"
[7 empty] | 115 |  |  |  |  | -6.53
276 |  | 122/1 | Gantry | -3.59 |  |  |  | 115 | 84610 | 74.53 | 0 |  | 175 | -45.5598 | 30.9075 | -14.6523 | -143.2117 | 31.7674 | -111.4443 |  |  |  | 93°49'48.5" | 26°57'46.5"
[7 empty] | 60 |  |  |  |  | -0.03 | [8 empty] | 400KV D/C Ranganadi -BaliparaT/L.
277 |  | 122/2 | Gantry | -3.59 |  |  |  | 60 | 84670 | 74.5 | 0 |  | 150 | 29.0925 | -17.5163 | 11.5762 | 28.2326 | -76.7521 | -48.5195 |  |  |  | 93°49'47.3" | 26°57'48.1"
[7 empty] | 90 |  |  |  |  | 3.1
278 | 123 | 123/0 | DD+0 | 0 |  | 12°0'18"RT |  | 90 | 84760 | 74.01 | 0 |  | 186 | 107.5163 | -6.0715 | 101.4447 | 166.7521 | -57.3058 | 109.4464 |  |  | DERGUWA | 93°49'45.5" | 26°57'50.6"
[7 empty] | 96 |  |  |  |  | 2.86
279 | 124 | 124/0 | DC+3 | 3 |  | 20°58'49"RT |  | 96 | 84856 | 73.87 | 0 |  | 396 | 102.0715 | 145.5835 | 247.6551 | 153.3058 | 141.3988 | 294.7046 |  |  | DERGUWA | 93°49'44.3" | 26°57'53.5"
[7 empty] | 300 |  |  |  |  | 0.73 | [8 empty] | 2 Nos Pond
280 |  | 124/1 | DA+0 | 0 | [5 empty] | 77.6 | 0 |  | 612 | 154.4165 | 150.2991 | 304.7155 | 158.6012 | 144.8973 | 303.4985 |  |  |  | 93°49'44.2" | 26°58'3.3"
[7 empty] | 312 |  |  |  |  | 0.98
281 |  | 124/2 | DA+0 | 0 | [5 empty] | 78.58 | 0 |  | 607 | 161.7009 | 144.1161 | 305.817 | 167.1027 | 140.9098 | 308.0125 |  |  |  | 93°49'44.2" | 26°58'13.4"
[7 empty] | 295 |  |  |  |  | 0.55 | [8 empty] | Pond
282 |  | 124/3 | DA+0 | 0 | [5 empty] | 79.13 | 0 |  | 599 | 150.8839 | 149.9701 | 300.854 | 154.0902 | 148.0467 | 302.1369 |  |  |  | 93°49'44.2" | 26°58'23"
[7 empty] | 304 |  |  |  |  | 0.34 | [8 empty] | Pond
283 |  | 124/4 | DA+0 | 0 | [5 empty] | 79.47 | 0 |  | 616 | 154.0299 | 147.0414 | 301.0713 | 155.9533 | 138.5529 | 294.5062 |  |  |  | 93°49'44.2" | 26°58'32.8"
[7 empty] | 312 |  |  |  |  | 1.54
284 |  | 124/5 | DA+0 | 0 | [5 empty] | 81.01 | 0 |  | 632 | 164.9586 | 140.3754 | 305.334 | 173.4471 | 121.7806 | 295.2277 |  |  |  | 93°49'44.2" | 26°58'43"
[7 empty] | 320 |  |  |  |  | 3.46 | [8 empty] | 11Kv, Metal Road
285 |  | 124/6 | DA+3 | 3 | [5 empty] | 81.47 | 0 |  | 595 | 179.6246 | 157.2999 | 336.9244 | 198.2194 | 176.0608 | 374.2801 |  |  |  | 93°49'44.1" | 26°58'53.3"
[7 empty] | 275 |  |  |  |  | -3 | [8 empty] | 11Kv
286 | 125 | 125/0 | DD+0 | 0 |  | 33°2'9"RT |  | 2118 | 86974 | 81.47 | 0 |  | 615 | 117.7001 | 137.9708 | 255.6709 | 98.9392 | 107.6223 | 206.5615 |  |  | 3 NO TATIBAHAR | 93°49'44.1" | 26°59'2.3"
[7 empty] | 340 |  |  |  |  | 6 | [8 empty] | LT Line, Vill Road
287 |  | 125/1 | DA+6 | 6 | [5 empty] | 81.47 | 0 |  | 682 | 202.0292 | 208.1489 | 410.1781 | 232.3777 | 243.3484 | 475.7262 |  |  |  | 93°49'50.8" | 26°59'11.6"
[7 empty] | 342 |  |  |  |  | -7
288 | 126 | 126/0 | DD+0 | 0 |  | 52°06'44"RT |  | 682 | 87656 | 80.47 | 0 |  | 557 | 133.8511 | 99.0582 | 232.9093 | 98.6516 | 91.0594 | 189.7109 |  |  | JARA BARI | 93°49'57.6" | 26°59'20.9"
[7 empty] | 215 |  |  |  |  | 1 | [8 empty] | 3 Nos Pond, 2Nos House, LT Line, Vill Road
289 | 127 | 127/0 | DC+3 | 3 |  | 18°06'41"LT |  | 215 | 87871 | 78.47 | 0 |  | 454 | 115.9418 | 140.4597 | 256.4015 | 123.9406 | 160.3196 | 284.2602 |  |  | JARA BARI | 93°50'5.3" | 26°59'21.5"
[7 empty] | 239 |  |  |  |  | -2.76 | [8 empty] | NH-15, 11Kv,2 Nos Boundary
290 | 128 | 128/0 | DD+0 | 0 |  | 49°45'28"RT |  | 239 | 88110 | 78.71 | 0 |  | 239 | 98.5403 | 72.2332 | 170.7735 | 78.6804 | 93.7735 | 172.4539 |  |  | JARA BARI | 93°50'13.3" | 26°59'24.5"
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN (M) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN (HOT) |  |  | WEIGHT SPAN IN (COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | EASTING | NORTHING
290 | 128 | 128/0 | DD+0 | 0 |  | 49°45'28"RT |  |  |  | 78.71 | 0 |  | 338 | 98.5403 | 72.2332 | 170.7735 | 78.6804 | 93.7735 | 172.4539 |  |  | JARA BARI | 93°50'13.3" | 26°59'24.5"
[7 empty] | 99 |  |  |  |  | -1.24
291 | 129 | 129/0 | DD+0 | 0 |  | 56°08'37"RT |  | 99 | 88209 | 77.47 | 0 |  | 183 | 26.7668 | 42 | 68.7668 | 5.2265 | 42 | 47.2265 |  |  | JARA BARI | 93°50'16.5" | 26°59'23.1"
[7 empty] | 84 |  |  |  |  | 0
292 | 130 | 130/0 | DD+0 | 0 |  | 14°54'06"RT |  | 84 | 88293 | 77.47 | 0 |  | 115 | 42 | 15.5 | 57.5 | 42 | 15.5 | 57.5 |  |  | JARA BARI | 93°50'16.9" | 26°59'20.4"
[7 empty] | 31 |  |  |  |  | 0
293 | BAY | BAY | Gantry | 0 |  |  |  | 31 | 88324 | 77.47 | 0 |  | 31 | 15.5 |  | 15.5 | 15.5 |  | 15.5 |  |  | JARA BARI | 93°50'16.7" | 26°59'19.4"
Note on D41: admin: +6 due wt. span
Note on D289: admin: +6 DUE TO WT SPAN
Note on G371: admin: ACTUAL ANGLE 14°48'34"LT
Note on G504: admin: ACTUAL ANGLE 29°46'02"RT
Note on D537: admin: +3 DUE TO WT SPAN
Note on G623: admin: actual angle 14°52'5"LT