## Annexure II (Erection)
ANNEXURE-II:
SCHEDULE OF QUANTITY (ERECTION AND CIVIL ITEMS) FOR 220/33KV BIHPURIA GIS
Sl. No. | Item Description | Required Quantity | Units
1 | 2 | 4 | 5
1 | Erection, testing and commissioning of 33kV,3 Phase, 13 Panel Indoor Drawn out type switchgear as per specification (Single bus with sectionalizer including 33kV PT) | 1 | Set
2 | Erection of Isolators
2.01 | Erection, testing and commissioning of 245KV, 3150A, Centre Break type Isolator with single earth switch complete with manual and motor driven operating mechanisms including laying and termination of LT power and control cables etc. as required. | 2 | Sets
2.02 | Erection, testing and commissioning of 33kV,1250A, 31.5kA for 3sec Double Break type Motorised Isolator with one earth switch along with Support Insulators, structures, Clamp & Connectors | 6 | Set
2.03 | Hoisting and erection of Insulators, Hardware Fittings & Stringing of Conductors
2.031 | 220kV, tension string insulators and hardwares suitable Twin MOOSE conductors | 6 | Set
2.032 | 220kV, Single suspension insulators and hardwares suitable Twin MOOSE conductors | 6 | Set
2.033 | 33 kV, Tension String insulators and hardwares suitable Panther conductors | 18 | Set
2.034 | 33 kV, Suspension String insulators and hardwares suitable Panther conductors | 18 | Set
2.035 | 4'' IPS Aluminium Tubular Conductors with flexi connectors, expansion joints, T- joints, end caps etc. | 250 | RM
2.036 | ACSR Twin Moose Conductor | 1.5 | KM
2.037 | ACSR Single Panther Conductor | 1 | KM
2.038 | Clamps & Connectors | 1 | LS
2.039 | 245KV, 1 phase Solid core bus post insulator with creepage distance 31mm/kV | 28 | No
3 | Service Transformer
3.01 | Erection, testing and commissioning of 250 KVA, 33/0.433kV Transformer, including Clamp & Connectors with Energy Efficiency level-III, BIS Clas-II including laying of connected power and control cables | 2 | Nos.
3.02 | Installation of 440V MCCB for Station Service Transformer | 6 | No.
3.03 | Installation of DO Fuse for Station Service Transformer | 2 | Set
4 | Surge Arrester
4.01 | Erection, testing and commissioning of 198kV, 10kA, LA complete with Surge Monitor, hardware fittings, clamp & connectors including laying and termination of LT power and control cables etc. as required. | 12 | No.
4.02 | Erection, testing and commissioning of 30kV, 10kA, LA with surge counter, hardware fittings, clamp & connectors including laying and termination of LT power and control cables etc. as required. | 30 | No.
5 | Inductive CVT and Wave Trap
5.01 | Erection, testing and commissioning of 220kV, 4400pF, 3 Wdg CVT, complete with hardware fittings, clamps & connectors including laying and termination of LT power and control cables etc. as required. | 6 | No.
5.02 | Erection, testing and commissioning of 220KV, 1250A Wave Trap including laying and termination of LT power and control cables etc. as required. | 4 | No
6 | Erection, testing and Commissioning of Control Relay & Protection Panel(Simplex type) including laying and termination of LT power and control cables etc. as required:
6.01 | 245 kV GIS
6.011 | Bus Bar Protection Panel | 1 | Nos
6.012 | Line Protection Panel with Auto Reclose and LBB | 2 | Nos.
6.013 | Transformer Protection Panel | 2 | Nos.
6.014 | Bus Coupler Protection Panel | 1 | Nos.
6.02 | 36kV Indoor AIS
6.021 | Line Protection Panel with LBB | 6 | Nos.
6.022 | Transformer Protection Panel | 2 | Nos.
6.023 | Bus Sectionaliser Panel | 1 | Nos.
6.024 | Station Service Transformer Panel | 2 | Nos.
7 | Installation and commissioning of Complete Substation Automation System (as per Technical Specification)
7.01 | Bay Control Units for 220kV Bays | 5 | Set
7.02 | Bay Control Units for 33kV Bays | 9 | Set
7.03 | Bay control Units for auxilary system | 2 | Set
7.04 | Station HMI (Main, Redundant and Metering) | 3 | Set
7.05 | Maintenance HMI (DR Workstation) | 1 | Set
7.06 | Gate way with PLCC and Fibre Optic Modem | 1 | Set
7.07 | Required UPS for 4 hour Back up | 1 | No
7.08 | Colour Laser Printer | 1 | Set
7.09 | Dot Matrix Printer | 1 | Set
7.1 | Line Printer | 1 | Set
7.11 | GPS Clock System | 1 | Set
7.12 | Ethernet Switch | 18 | Nos.
7.13 | All interphase equipment for Gateway to SLDC | 1 | Set
7.14 | All other accessories like FO armoured cables, Patch cords,furnitures for HMIs and printers, cables etc | 1 | LS
8 | Erecton, testing and commissioning of following GIS modules including laying and termination of LT power and control cables etc. as required:
8.01 | 245kV, 50kA for 3 second, SF6 gas-insulated metal enclosed Line bay module each set comprising of One (1) number 3-phase, 3150A, SF6 insulated circuit breaker complete with operating mechanism; Three (3) numbers 1-phase, 6-core, multi ratio, 1000-800/1-1-1-1-1-1A current transformers; Three (3) numbers 3-phase, 3150A, group operated isolators/disconnectors, complete with manual and motor driven operating mechanisms; One (1) number 3-phase, group operated safety grounding switches, complete with manual and motor driven operating mechanisms; One (1) number 3-phase, high speed fault make grounding switch, complete with group operated manual and motor driven operating mechanisms; Three nos. 1-phase (isolated) SF6 ducts inside GIS hall (upto the outer edge of the wall of GIS Hall) along with terminations for connecting with outside busduct; Gas monitoring devices, barriers, pressure switches UHF PD Sensors, support structure etc. as required; Local Bay control cubicle.(Stand Alone) | 2 | Sets
8.02 | 245kV, 50kA for 3 second, SF6 gas-insulated metal enclosed Transformer bay module each set comprising of One (1) number 3-phase, 3150A, SF6 insulated circuit breaker complete with operating mechanism; Three (3) numbers 1-phase, 6-core, multi ratio,600-300/1-1-1-1-1-1A current transformers; Three (3) numbers 3-phase, 3150A, group operated isolators/disconnectors, complete with manual and motor driven operating mechanisms; One (1) number 3-phase, group operated safety grounding switches, complete with manual and motor driven operating mechanisms; Three nos. 1-phase (isolated) SF6 ducts inside GIS hall (upto the outer edge of the wall of GIS Hall) along with terminations for connecting with outside bus duct; Gas monitoring devices, barriers, pressure switches UHF PD Sensors, support structure etc. as required; Local Bay control cubicle.(Stand Alone) | 2 | Sets
8.03 | 245kV, 50kA for 3 second, SF6 gas-insulated metal enclosed Bus Coupler bay module each set comprising of One (1) number 3-phase, 3150A, SF6 insulated circuit breaker complete with operating mechanism; Three (3) numbers 1-phase, 4-core, multi ratio, 1000-800/1-1-1-1A current transformers; Two (2) numbers 3-phase,3150A, group operated isolator switches, complete with manual and motor driven operating mechanisms; Four (4) numbers 3-phase, single pole group operated safety grounding switches, complete with manual and motor driven operating mechanisms; Gas monitoring devices, barriers, pressure switches UHF PD Sensors, support structure etc. as required; Local Bay control cubicle. (Stand Alone) | 1 | Sets
8.04 | Three phase, 3150A, 50kA for 3 second, SF6 gas-insulated metal enclosed bus bar of 245kV, each set comprising of Bus bars enclosures running across the length of the switchgear to interconnect each of the circuit breaker bay modules in Double Bus bar configuration; One (1) number 3-phase, 3150A, group operated isolator switches, complete with manual and motor driven operating mechanisms for Bus VT bay; One (1) number 3-phase, group operated safety grounding switches for Bus VT bay, complete with manual and motor driven operating mechanisms; Three (3) numbers 1-phase Potential Transformers complete with isolator switch/link, Gas monitoring devices, barriers, pressure switches, UHF PD Sensors, support structure etc. as required, local bay control cubicle for VT (Standalone) | 2 | sets
8.05 | 245kV, 1600A, 50 kA for 3 sec, 1- phase SF6/ air bushings along with termination module & support structure for outdoor connections to connect GIS with 245kV side of Powertransformer and overhead lines. | 12 | Nos
8.06 | 245kV, 1600A, 50kA for 3 second, 1-Ph, SF6 Gas Insulated Bus Duct (GIB) outside GIS hall including Bus Duct support structure and associated accessories | 700 | Running Meter
8.07 | 7.5 Ton EOT Crane for 245kV GIS Building | 1 | No.
9 | Erection, testing and Commissioning of 100MVA, 220/33kV, ONAN/ONAF/OFAF, Power Transformer along with all accessories as below:-(3 ph, 50 Hz, 2 winding Star/Star, Vector Group: YNyn0) including associated fire protection scheme and laying and terminating all signalling and control cables
9.01 | 100 MVA, 220/33 kV, Three phase Transformer with OLTC | 2 | Set
9.02 | Oil & winding temperature monitoring system (FO based) | 2 | Set
9.03 | Nitrogen injection Fire prevention system/ HVWS | 2 | Set
9.04 | Portable/Online DGA/Online insulating drying system for above transformer | 2 | Set
9.05 | Digital RTCC Panel | 2 | Set
9.06 | Terminal connector on 220kV side bushing of 220/33kV Transformer to suit Twin Moose conductor | 6 | Nos.
9.07 | Terminal connector on 33kV side bushing of 220/33kV Transformer to suit 4'' IPS Aluminium Tubular Conductors | 6 | Nos.
9.08 | Single phase HV side bushing phase CT (300/1A, 3 core) | 6 | Nos.
9.09 | Single phase LV side bushing phase CT (2000/1A, 3 core) | 6 | Nos.
9.1 | Single phase HV side bushing mounted NCT (300/1A, 2 core) | 2 | Nos.
9.11 | Single phase LV side bushing mounted NCT (2000/1A, 2 core) | 2 | Nos.
10 | Erection, testing and Commissioning of Battery & Battery Chargers, DCDB & ACDB and other panels and accesories including laying of connected cables with terminations
10.01 | 220V VRLA Battery, 500AH | 2 | Set
10.02 | 220V, Dual Float Cum Boost Chargers, 120A | 2 | Set
10.03 | 220V, DCDB | 2 | Set
10.04 | 48V VRLA type Battery Bank, 300 AH | 2 | Set
10.05 | 48V, Float cum Boost Chargers, 150AH | 2 | Set
10.06 | 48V, DCDB | 2 | Set
10.07 | Main ACDB | 2 | Set
10.08 | Sub ACDB | 2 | Nos.
10.09 | MLDB | 1 | Set
10.1 | ELDB | 1 | Set
10.11 | HVAC DB | 1 | Set
10.12 | MCBDB | 1 | Set
11 | Installation and commissioning of all equipment complete with erection of mounting structures, laying and terminations of all cables including construction of foundations and supply of foundation materials as required for PLCC System links (excluding CVT)
11.01 | HF co-axial cable | 500 | METER
11.02 | Digital Carrier Equipment Panel | 4 | No.
11.03 | Digital Protection Coupler/ Tele protection coupler | 4 | No.
11.04 | EPAX system | 1 | No.
11.05 | LMU/ LMDU | 2 | SET
11.06 | Audio Cable | 100 | meter
11.07 | Two wire telephone set | 2 | No
12 | XLPE Cable and Termination Kit as per specification no. Of Vol 2
12.01 | Laying of 1000 sqmm, 1-Core, XLPE Armoured Cu cable alongwith related accessories in cable trenches and cable terminations including supply of cable end sealing boxes, construction of cable trenches etc. | 2500 | meter
12.02 | Erection, testing and commissioning of 33kV Cable Termination Kit along with its accessories and one number spare | 40 | No.
13 | Installation of complete earthing system including supply of all earthing materials
13.01 | Main earth mat conductor, GI risers, treated /Untreated earth pit, equipment earth connections etc.
13.011 | Main Earthing Conductor 75X12 Mm GI Flat | 12000 | LS(Mtrs)
13.012 | Earthing Conductor: 75X 10 Mm Gi (HDG) Flat For Riser From The Burial Earth Mat To Equipment,Structure Etc) | 4000 | LS(Mtrs)
13.013 | Earthing Conductor: 50X10 Mm Gi (HDG) Flat For Riser For Console Box,Lt Panels,Dc Panels,Marshalling Boxes, Cable Trenches Etc) | 2000 | LS(Mtrs)
13.014 | Earthing Device & Associated Accessories (50 Mm Heavy Duty Gi Perforated Pipe 3 Mtrs Long For Treated Earth Pit) | 120 | LS (Nos)
13.015 | Earthing Device & Associated Accessories 40Mm Ms Rod 3 Mtrs Long For Non Treated Earth Pit) | 100 | LS(Nos)
13.016 | Soil Resistivity Test And Soil Treatment As And When Required | 1 | JOB
13.017 | Separate Earthing For 245 Kv GIS Modules | 1 | JOB
13.018 | Separate Earthing For GIS Building | 1 | JOB
13.019 | Separate Earthing For 36 Kv Indoor AIS | 1 | JOB
13.02 | Separate Earthing For 36 Kv Indoor AIS Building | 1 | JOB
13.021 | Separate Earthing For Fencing Around The Substation | 1 | JOB
13.022 | Other Earthing Accessories | 1 | Lot
14 | Erection of lattice Steel Structures and Mounting structures
14.01 | Lattice structures (MS steel) for incoming and outgoing gantries etc
14.011 | Erection of 220kV Column type 'C3' | 3 | Nos
14.012 | Construction of foundations for lattice steel columns 'C3' including supply of all foundation materials and labour | 1 | Lot
14.013 | Erection of 220kV Beam type 'B3' | 2 | Nos
14.014 | Erection of 33kV Column type 'C5' | 8 | Nos
14.015 | Construction of foundations for lattice steel columns 'C5' including supply of all foundation materials and labour | 1 | Lot
14.016 | Erection of 33kV Beam type 'B5' | 6 | Nos
14.017 | Erection of Pipe structures | 1 | Lot
14.018 | Erection of Foundation Bolts (Including nuts,checknut & washers for lattice and pipe structures) | 1 | Lot
14.019 | Erection of Fastners(nuts, bolts and washers) including step bolts for lattice and pipe structures | 1 | Lot
14.02 | Mounting structures for equipments
14.021 | Erection of mounting structures as required for 245 KV Centre Break type Motorised Isolators including construction of foundation and supply of all foundation materials | 6 | Nos
14.022 | Erection of mounting structures as required for 33 KV Double Break type Motorised Isolators including construction of foundation and supply of all foundation materials | 18 | Nos
14.023 | Erection of mounting structures as required for 198KV lightning arrester including construction of foundation and supply of all foundation materials | 12 | No.
14.024 | Erection of mounting structures as required for 30 kV LA including construction of foundation and supply of all foundation materials | 30 | No.
14.025 | Erection of mounting structures as required for 220kV, 4400pF, 3 Wdg CVT including construction of foundation and supply of all foundation materials | 6 | No
14.026 | Erection of Mounting structures of Post Insulators as required including construction of foundation and supply of all foundation materials | 28 | No
15 | Design, construction and installation of HVAC & VENTILATION
15.01 | 2 TON CAPACITY SPLIT AIR CONDITIONING UNITS for Control Room Buildings | 1 | Lot
15.02 | Ventilation system for 245kV GIS Building (Ventilation System with Centrifugal Fan and related Accessories should comprise of Pre and Fine air filter, centrifugal fan, ducting network, air supply grilles, gravity dampers, electrical and instrumentation etc.) | 1 | Lot
16 | Design, construction and installation of Fire Alarm & Detection
16.01 | Fire Alarm & Detection system for 245kV GIS Buildings, Control Room building including Fire Alarm panel, Multi Sensor detector, manual Call point, Hooter, Response Indicators, Beam Detector, Cabling and ISOLATING MODULE | 1 | Lot
17 | Design, construction and installation of Hydrant & HVWS (High Velocity Water Spray) system/ NIFPES
17.01 | Hydrant system along with pumping arrangement & associated Civil works for fire protection system | 1 | Lot
17.02 | HVWS system for 100 MVA ICT-2 No’s | 1 | Lot
17.03 | Nitrogen injection fire protection and emergency services with complete accessories and related civil and electrical works. | 1 | Lot
18 | Erection, testing and commissioning of 100 KVA, DG Set with AMF including Panel & Accessories and related foundation works | 1 | Set
19 | Design, construction and installation of LIGHTING SYSTEM
19.01 | Indoor Lighting
19.011 | Lighting System including Lighting panel, Cabling, Conduiting, Switches, Socket, Junction boxes, auxiliary receptacle, High bay fixtures for GIS rooms
19.0111 | 245 kV GIS Building | 1 | Lot
19.0112 | Control Room Building | 1 | Lot
19.0113 | Pump House | 1 | Lot
19.0114 | Security booth | 1 | Lot
19.0115 | Security barrack | 1 | Lot
19.0116 | Staff hostel, Officer hostel cum Transit camp | 1 | Lot
19.0117 | Store building | 1 | Lot
19.0118 | open store shed | 1 | Lot
19.012 | Outdoor Lighting
19.0121 | Outdoor LED lighting for Switchyard, Road area, Car parking, Security outpost including Lighting panel, Cabling, Switches, Socket, auxiliary receptacle, complete with GI Poles etc. | 1 | Lot
20 | Installation of Public Addressing System, CCTV | 1 | Lot
21 | Erection of Lightning Protection Equipments (lightning masts, lightning spikes, shield wires, down conductors etc.) and its accessories including construction of foundations and supply of foundation materials along with complete earthing arrangement. | 1 | Lot
22 | CIVIL WORK (As per technical specification)
22.01 | Soil Investigation | 1 | Job
22.02 | Standards, Design And Drawings | 1 | Job
22.03 | Site Clearance including necessary excavation | 1 | Job
22.04 | Site Preparation and Earthfilling with Compaction | 64670 | cum
22.05 | Boundary Wall | 837 | Rm
22.06 | Buildings (including All services i.e. electrical, internal water supply and sanitary works complete)
22.061 | 220 KV GIS Building alongwith GIS bay foundations complete | 1 | Each
22.062 | 33kV Switchgear & Control Room building | 1 | Each
22.063 | RE's Residence | 1 | Each
22.064 | Office's Hostel cum Transit Camp | 1 | Each
22.065 | Staff Hostel and quarters | 1 | Each
22.066 | Store Building | 1 | Each
22.067 | Open store shed | 1 | Each
22.07 | Construction of Transformer pad for 220/33KV, 100MVA Transformer with oil pit | 2 | No
22.08 | Construction of 250KVA, 33/0.4KV Statiion Transformer pad | 2 | No
22.09 | Fire Protection Wall | 2 | No
22.1 | Construction of cable trench as per technical specification
22.101 | Type-D | 100 | RM
22.102 | Type-C | 400 | RM
22.11 | Drain
22.111 | Storm Water Drain | 1215 | Rm
22.112 | Sewage Drain | 105 | Rm
22.113 | Sump Pit | 3 | Nos.
22.12 | Antiweed treatment | 4092 | Sq. m.
22.13 | PCC in Switchyard | 4092 | Sq. m.
22.14 | Stone Spreading(Gravelling) in switchyard | 4092 | Sq. m.
22.15 | Switchyard Security Fencing | 55 | Rm
22.16 | Security Gate for switchyard and colony | 3 | Nos.
22.17 | Roads (Inter locking Cement Concrete Block Road)
22.171 | 6 m Wide | 3126 | SqMeter
22.172 | 5 m Wide | 400 | SqMeter
22.173 | 4 m Wide | 580 | SqMeter
22.18 | RCC Box Culvert | 3 | Nos.
22.19 | Water Tank & Pump House (including Bore well, Slow sand filter, iron removal filter, OH Tank, Pumps, external pipes and fittings) (with connection to all buildings and garden area) | 1 | Job
22.2 | Security Barrack | 1 | Each
22.21 | Security Booth for colony and switchyard | 2 | Each
22.22 | Car Parking shed (5.5m x 3m) | 5 | Nos.
22.23 | Car Parking Area | 500 | SqMeter
22.24 | Landscaping, Garden & Plantation | 1 | Job
22.25 | Rain Water Harvesting | 1 | Job
23 | ESMP Requirement
23.01 | Personal protective equipment’s (Hard hats (with full/partial brims as necessary) Safety glasses with side shields. Face masks/shields. Suitable footwear (safety/steel-toed boots, rated dielectric footwear) Insulating gloves (rated, used along with leather/cloth linings for shock protection)) as per site requirement | 1 | Lot
23.02 | SF6 retrieving arrangement as per site requirement | 1 | Lot
23.03 | Wire insulation/ Bird Deflectors/ Bird Flapper as per requirement including installation | 1 | Lot