## Annexure I (Supply)
ANNEXURE-I:
SCHEDULE OF QUANTITY (SUPPLY) INCLUDING MANDATORY SPARE PARTS FOR 220/33KV BIHPURIA GIS
Sl. No. | Item Description | Required Quantity | Units
1 | 2 | 4 | 5
1 | 33kV,3 Phase, 13 Panel Indoor Drawn out type switchgear as per specification (Single bus with sectionalizer including 33kV PT) | 1 | Set
2 | Isolators
2.01 | 245KV, 3150A, Centre Break type Isolator with single earth switch complete with manual and motor driven operating mechanisms | 2 | Sets
2.02 | 33kV,1250A, 31.5kA for 3sec Double Break type Motorised Isolator with one earth switch along with Support Insulators, structures, Clamp & Connectors | 6 | Set
2.03 | Insulators, hardware & Conductors
2.031 | 220kV, tension string insulators and hardwares suitable Twin MOOSE conductors | 6 | Set
2.032 | 220kV, Single suspension insulators and hardwares suitable Twin MOOSE conductors | 6 | Set
2.033 | 33 kV, Tension String insulators and hardwares suitable Panther conductors | 18 | Set
2.034 | 33 kV, Suspension String insulators and hardwares suitable Panther conductors | 18 | Set
2.035 | 4'' IPS Aluminium Tubular Conductors with flexi connectors, expansion joints, T- joints, end caps etc. | 250 | RM
2.036 | ACSR Twin Moose Conductor | 1.5 | KM
2.037 | ACSR Single Panther Conductor | 1 | KM
2.038 | Clamps & Connectors | 1 | LS
2.039 | 245KV, 1 phase Solid core bus post insulator with creepage distance 31mm/kV | 28 | No.
3 | Station Service Transformer
3.01 | 250 KVA, 33/0.433kV StationTransformer, including Clamp & Connectors with Energy Efficiency level-III, BIS Clas-II | 2 | Nos.
3.02 | 440V MCCB for Station Service Transformer | 6 | Nos.
3.03 | 33kV DO Fuse | 2 | Set
4 | Surge Arrester
4.01 | 198kV, 10kA, LA complete with Surge Monitor, hardware fittings, clamp & connectors as per specification | 12 | No.
4.02 | 30kV, 10kA, LA with surge counter, hardware fittings, clamp & connectors as per specification no. | 30 | No.
5 | Inductive CVT and Wave Trap
5.01 | 220kV, 4400pF, 3 Wdg CVT, complete with hardware fittings, clamps & connectors | 6 | No.
5.02 | 220KV, 1250A Wave Trap | 4 | No.
6 | Control Relay & Protection Panel(Simplex Type)
6.01 | 245kV GIS
6.011 | Bus Bar Protection Panel | 1 | No.
6.012 | Line Protection Panel with Auto Reclose and LBB | 2 | Nos.
6.013 | Transformer Protection Panel | 2 | Nos.
6.014 | Bus Coupler Protection Panel | 1 | No.
6.02 | 36kV Indoor AIS
6.021 | Line Protection Panel with LBB | 6 | Nos.
6.022 | Transformer Protection Panel | 2 | Nos.
6.023 | Bus Sectionaliser Panel | 1 | No.
6.024 | Station Service Transformer Panel | 2 | Nos.
7 | Complete Substation System Automation System (As per specification )
7.01 | Bay Control Units for 220kV Bays | 5 | Set
7.02 | Bay Control Units for 33kV Bays | 9 | Set
7.03 | Bay control Units for auxilary system | 2 | Set
7.04 | Station HMI (Main, Redundant and Metering) | 3 | Set
7.05 | Maintenance HMI (DR Workstation) | 1 | Set
7.06 | Gate way with PLCC and Fibre Optic Modem | 1 | Set
7.07 | Required UPS for 4 hour Back up | 1 | No
7.08 | Colour Laser Printer | 1 | Set
7.09 | Dot Matrix Printer | 1 | Set
7.1 | Line Printer | 1 | Set
7.11 | GPS Clock System | 1 | Set
7.12 | Ethernet Switch | 18 | Nos.
7.13 | All interphase equipment for Gateway to SLDC | 1 | Set
7.14 | All other accessories like FO armoured cables, Patch cords,furnitures for HMIs and printers, cables etc | 1 | LS
8 | 245 kV GIS Equipment
8.01 | 245kV, 50kA for 3 second, SF6 gas-insulated metal enclosed Line bay module each set comprising of One (1) number 3-phase, 3150A, SF6 insulated circuit breaker complete with operating mechanism; Three (3) numbers 1-phase, 6-core, multi ratio, 1000-800/1-1-1-1-1-1A current transformers; Three (3) numbers 3-phase, 3150A, group operated isolators/disconnectors, complete with manual and motor driven operating mechanisms; One (1) number 3-phase, group operated safety grounding switches, complete with manual and motor driven operating mechanisms; One (1) number 3-phase, high speed fault make grounding switch, complete with group operated manual and motor driven operating mechanisms; Three nos. 1-phase (isolated) SF6 ducts inside GIS hall (upto the outer edge of the wall of GIS Hall) along with terminations for connecting with outside busduct; Gas monitoring devices, barriers, pressure switches UHF PD Sensors, support structure etc. as required; Local Bay control cubicle.(Stand Alone) | 2 | Sets
8.02 | 245kV, 50kA for 3 second, SF6 gas-insulated metal enclosed Transformer bay module each set comprising of One (1) number 3-phase, 3150A, SF6 insulated circuit breaker complete with operating mechanism; Three (3) numbers 1-phase, 6-core, multi ratio,600-300/1-1-1-1-1-1A current transformers; Three (3) numbers 3-phase, 3150A, group operated isolators/disconnectors, complete with manual and motor driven operating mechanisms; One (1) number 3-phase, group operated safety grounding switches, complete with manual and motor driven operating mechanisms; Three nos. 1-phase (isolated) SF6 ducts inside GIS hall (upto the outer edge of the wall of GIS Hall) along with terminations for connecting with outside bus duct; Gas monitoring devices, barriers, pressure switches UHF PD Sensors, support structure etc. as required; Local Bay control cubicle.(Stand Alone) | 2 | Sets
8.03 | 245kV, 50kA for 3 second, SF6 gas-insulated metal enclosed Bus Coupler bay module each set comprising of One (1) number 3-phase, 3150A, SF6 insulated circuit breaker complete with operating mechanism; Three (3) numbers 1-phase, 4-core, multi ratio, 1000-800/1-1-1-1A current transformers; Two (2) numbers 3-phase,3150A, group operated isolator switches, complete with manual and motor driven operating mechanisms; Four (4) numbers 3-phase, single pole group operated safety grounding switches, complete with manual and motor driven operating mechanisms; Gas monitoring devices, barriers, pressure switches UHF PD Sensors, support structure etc. as required; Local Bay control cubicle. (Stand Alone) | 1 | Sets
8.04 | Three phase, 3150A, 50kA for 3 second, SF6 gas-insulated metal enclosed bus bar of 245kV, each set comprising of Bus bars enclosures running across the length of the switchgear to interconnect each of the circuit breaker bay modules in Double Bus bar configuration; One (1) number 3-phase, 3150A, group operated isolator switches, complete with manual and motor driven operating mechanisms for Bus VT bay; One (1) number 3-phase, group operated safety grounding switches for Bus VT bay, complete with manual and motor driven operating mechanisms; Three (3) numbers 1-phase Potential Transformers, Gas monitoring devices, barriers, pressure switches, UHF PD Sensors, support structure etc. as required, local bay control cubicle for VT (Standalone) | 2 | sets
8.05 | 245kV, 1600A, 50 kA for 3 sec, 1- phase SF6/ air bushings along with termination module & support structure for outdoor connections to connect GIS with 245kV side of Powertransformer and overhead lines. | 12 | Nos
8.06 | 245kV, 1600A, 50kA for 3 second, 1-Ph, SF6 Gas Insulated Bus Duct (GIB) outside GIS hall including Bus Duct support structure and associated accessories | 700 | Running Meter
8.07 | 7.5 Ton EOT Crane for 245kV GIS Building | 1 | No.
9 | Supply, Testing And Maintenance Equipment of GIS as specified
9.01 | SF6 Gas Processing, Drying, Storage & Filling Unit | 1 | No.
9.02 | Online Partial Discharge Monitoring Unit | 1 | No.
9.03 | SF6 gas quality testing unit | 1 | No.
9.04 | SF6 Gas Leak Detector | 1 | No.
9.05 | Precision Pressure Gauge | 1 | No.
9.06 | SF6 Gas Evacuation Plant (One mobile cart and one static cart) | 2 | No.
9.07 | Video Borescope | 1 | No.
9.08 | SF6 gas Mask | 10 | No.
10 | 100MVA, 220/33kV, ONAN/ ONAF/OFAF, Power Transformer along with all accessories as below:- (3 ph, 50 Hz, 2 winding Star/Star, Vector Group: YNyn0 as specified
10.01 | 100 MVA, 220/33 kV, Three phase Transformer with OLTC | 2 | Set
10.02 | Oil & winding temperature monitoring system (FO based) | 2 | Set
10.03 | Nitrogen injection Fire prevention system/ HVWS | 2 | Set
10.04 | Online DGA | 2 | Set
10.05 | Online insulating drying system | 2 | Set
10.06 | Digital RTCC Panel | 1 | LS
10.07 | 10% Extra OIL for each transformer | 6 | No.
10.08 | Terminal connector on 220kV side bushing of 220/33kV Transformer to suit Twin Moose conductor | 6 | No.
10.09 | Terminal connector on 33kV side bushing of 220/33kV Transformer to suit 4'' IPS Aluminium Tubular Conductors | 6 | Nos.
10.1 | Single phase HV side 3 core bushing phase CT (300/1A, 2 core) and 1 core for WTI | 6 | Nos.
10.11 | Single phase LV side 3 core bushing phase CT (2000/1A, 2 core) and 1 core for WTI | 2 | Nos.
10.12 | Single phase HV side bushing mounted NCT (300/1A, 2 core) | 2 | Nos.
10.13 | Single phase LV side bushing mounted NCT (2000/1A, 2 core) | 2 | Nos.
11 | Battery & Battery Chargers, DCDB & ACDB as per specification
11.01 | 220V VRLA Battery, 500AH | 2 | Set
11.02 | 220V, Dual Float Cum Boost Chargers, 120A | 2 | Set
11.03 | 220V, DCDB | 2 | Set
11.04 | 48V VRLA type Battery Bank, 300 AH | 2 | Set
11.05 | 48V, Float cum Boost Chargers, 150AH | 2 | Set
11.06 | 48V, DCDB | 2 | Set
11.07 | Main ACDB | 2 | Set
11.08 | Sub ACDB | 2 | No.
11.09 | MLDB | 1 | Set
11.1 | ELDB | 1 | Set
11.11 | HVAC DB | 1 | Set
11.12 | MCBDB | 1 | Set
12 | Power Line Carrier Communication Equipments (Twin Channel, 8kHz)
12.01 | HF co-axial cable | 500 | meter
12.02 | Digital Carrier Equipment Panel | 4 | No
12.03 | Digital Protection Coupler/ Tele protection coupler | 4 | No
12.04 | EPAX system | 1 | No
12.05 | LMU/ LMDU | 2 | Set
12.06 | Audio Cable | 100 | meter
12.07 | Two wire telephone set | 2 | No
13 | XLPE Cable and Termination Kit as per specification
13.01 | 1000 sqmm, 1-Core, XLPE Armoured Cu cable alongwith related accessories | 2500 | meter
13.02 | 33kV Cable Termination Kit along with its accessories and one number spare | 40 | No.
14 | LT Power Cable
14.01 | 2C, 6mmsq | 1000 | meter
14.02 | 4C, 16mmsq | 1000 | meter
14.03 | 3.5C, 35mmsq | 1000 | meter
14.04 | 3.5C, 70mmsq | 1000 | meter
14.05 | 3.5C, 300mmsq | 1000 | meter
14.06 | Cable supports | 1 | Lot
15 | LT Control Cable
15.01 | 2C, 1.5mmsq | 500 | meter
15.02 | 4C, 2.5mmsq | 500 | meter
15.03 | 7C, 1.5mmsq | 500 | meter
15.04 | 12C, 1.5mmsq | 500 | meter
15.05 | 19C, 1.5mmsq | 500 | meter
16 | Earthing
16.01 | Main earth mat conductor, GI risers, treated /Untreated earth pit, equipment earth connections etc.
16.011 | Main Earthing Conductor 75X12 Mm GI Flat | 12000 | LS(Mtrs)
16.012 | Earthing Conductor: 75X 10 Mm GI (HDG) Flat For Riser From The Burial Earth Mat To Equipment,Structure Etc) | 4000 | LS(Mtrs)
16.013 | Earthing Conductor: 50X10Mm GI(HDG) Flat For Riser For Console Box,Lt Panels,Dc Panels,Marshalling Boxes, Cable Trenches Etc) | 2000 | LS(Mtrs)
16.014 | Earthing Device & Associated Accessories (50 Mm Heavy Duty Gi Perforated Pipe 3 Mtrs Long For Treated Earth Pit) | 120 | LS (Nos)
16.015 | Earthing Device & Associated Accessories 40Mm Ms Rod 3 Mtrs Long For Non Treated Earth Pit) | 100 | LS(Nos)
16.016 | Soil Resistivity Test And Soil Treatment As And When Required | 1 | JOB
16.017 | Separate Earthing For 245 Kv GIS Modules | 1 | JOB
16.018 | Separate Earthing For GIS Building | 1 | JOB
16.019 | Separate Earthing For 36 Kv Indoor AIS | 1 | JOB
16.02 | Separate Earthing For 36 Kv Indoor AIS Building | 1 | JOB
16.021 | Separate Earthing For Fencing Around The Substation | 1 | JOB
16.022 | Other Earthing Accessories | 1 | Lot
17 | Lattice Structures (MS Steel) for incoming and outgoing gantries etc
17.01 | 220kV Column type 'C3' | 3 | Nos.
17.02 | 220kV Beam type 'B3' | 2 | Nos.
17.03 | 33kV Column type 'C5' | 8 | Nos.
17.04 | 33kV Beam type 'B5' | 6 | Nos.
17.05 | Pipe structures | 1 | LS
17.06 | Foundation Bolts (Including nuts,checknut & washers for lattice and pipe structures) | 1 | LS
17.07 | Fastners(nuts, bolts and washers) including step bolts for lattice and pipe structures | 1 | LS
18 | HVAC & VENTILATION
18.01 | 2 TON CAPACITY SPLIT AIR CONDITIONING UNITS for Control Room Building | 1 | Lot
18.02 | Ventilation system for 245kV GIS Building (Ventilation System with Centrifugal Fan and related Accessories should comprise of Pre and Fine air filter,Air Purifier, centrifugal fan, ducting network, air supply grilles, gravity dampers, electrical and instrumentation etc.) | 1 | Lot
19 | Fire Alarm & Detection200
19.01 | Fire Alarm & Detection system for 245kV GIS Buildings, Control Room building including Fire Alarm panel, Multi Sensor detector, manual Call point, Hooter, Response Indicators, Beam Detector, Cabling and ISOLATING MODULE | 1 | Lot
20 | Hydrant & HVWS (High Velocity Water Spray) system/NIFPES
20.01 | Hydrant system along with pumping arrangement & associated Civil works for fire protection system | 1 | Lot
20.02 | HVWS system for 100 MVA ICT-2 No’s | 1 | Lot
20.03 | NItrogen injection Fire protection and emergency service with complete accessories and related Civil and Electrical works | 1 | Lot
21 | 100 KVA, DG Set with AMF including Panel & Accessories including earthing arrangement | 1 | set
22 | Lighting System
22.01 | Indoor Lighting
22.011 | Lighting System including Lighting panel, Cabling, Conduiting, Switches, Socket, Junction boxes, auxiliary receptacle, High bay fixtures for GIS rooms
22.0111 | 245 kV GIS Building | 1 | Lot
22.0112 | Control Room Building | 1 | Lot
22.0113 | Pump House | 1 | Lot
22.0114 | Security booth | 1 | Lot
22.0115 | Security barrack | 1 | Lot
22.0116 | Staff hostel, Officer hostel, Transit camp | 1 | Lot
22.02 | Outoor Lighting
22.021 | Outdoor LED lighting for Switchyard, Road area, Car parking, Security outpost including Lighting panel, Cabling, Switches, Socket, auxiliary receptacle, complete with GI Poles etc. | 1 | Lot
23 | Public Addressing System, CCTV | 1 | Lot
24 | Lightning protection (lightning masts, Lightning Spike, shield wire, down conductors etc.) | 1 | Lot
25 | Mandatory spares
25.01 | For 245KV GIS
25.011 | 245KV Gas Insulated Single phase voltage transformer with enclosure | 1 | SET
25.012 | 245KV Gas Insulated Single phase Current transformer with enclosure | 1 | SET
25.013 | SF6 gas Pressure relief devices 1 no each type for 245KV GIS | 1 | SET
25.014 | SF6 Pressure gauges cum switch or Density Monitors and pressure switches for 245KV GIS : 1 no. of each type | 1 | SET
25.015 | Coupling device for pressure gauge cum switch for connecting gas handling plant | 1 | SET
25.016 | Rubber gaskets, 'O'-ring and seals for SF6 gas of each type | 1 | SET
25.017 | Trip coil assembly with resistor for 245KV GIS Circuit breaker (2 nos. of each type) | 1 | SET
25.018 | Closing coil assembly with resistor for 245KV GIS Circuit breaker (2 nos. of each type) | 1 | SET
25.019 | Molecular filter for SF6 gas modules with filter bags, 20% of total weight | 1 | LOT
25.02 | Molecular filter for SF6 circuit breaker with filter bags, 10% of total weight | 1 | LOT
25.021 | All types of control valves for SF6 gas of each type for 245KV GIS | 1 | SET
25.022 | Locking device to keep the Disconnectors and Earthing switches in close or Open position in case of removal of removal of driving mechanism for 245KV GIS. | 1 | SET
25.023 | SF6 to Air bushing as applicable for 245KV GIS | 1 | SET
25.024 | Complete circuit breaker poles of each type and rating complete with interrupter, main circuit, enclosures and marshalling box with operating mechanism ( 1 no. of each type and rating) | 1 | LOT
25.025 | Set of spares for local control cabinet including M.C.B., fuses, time relays,all type of auxiliary relay & contactors,lamps,semaphor,terminals, push buttons etc for 245KV GIS | 1 | SET
25.026 | SF6 Pressure gauges cum switch or Density Monitors and pressure switches for SF6 Circuit breaker : 1 no. of each type | 1 | SET
25.027 | Coupling device for pressure gauge cum switch for connecting gas handling plant for SF6 circuit breaker (2 no. of each type) | 1 | SET
25.028 | Fixed, moving and arcing contacts for SF6 circuit breaker including insulating nozzles (3 nos. of each type) | 1 | LOT
25.029 | Auxiliary contacts for 245KV GIS circuit breaker | 1 | SET
25.03 | Auxiliary switch assembly for SF6 circuit breaker 2 nos of each type | 1 | LOT
25.031 | Limit switch & Auxiliary contacts for 245KV GIS DS and ES | 1 | SET
25.032 | Rubber gaskets, 'O'-ring and seals for SF6 circuit breaker (1 no. each type) | 1 | LOT
25.033 | Operation counter of SF6 circuit breaker 2 nos. of each type | 1 | LOT
25.034 | SF6 gas in steel bottle (20% of total weight) | 1 | LOT
25.035 | All types of coupling for SF6 gas (2 no. of each type) | 1 | SET
25.036 | spring charge motor for 245KV GIS circuit breakers | 1 | SET
25.02 | For spring operating mechanism of 245KV
25.021 | Complete spring operating mechanism 2 nos. of each type | 1 | SET
25.022 | Closing dashpot | 1 | SET
25.023 | Opening dashpot | 1 | SET
25.024 | Opening catch gear | 1 | SET
25.025 | Closing catch gear | 1 | SET
25.026 | Pipe length (copper/ steel as applicable) for SF6 circuit of each type | 1 | SET
25.027 | Relays, power contactors, push buttons, timers and MCBs etc of each type and rating | 1 | SET
25.028 | Windowscope/ observing window 2 nos. each type | 1 | SET
25.029 | Complete Drive for 245KV GIS circuit breaker: | 1 | SET
25.03 | Complete drive mechanism for disconnect switches and grounding switches for 245KV GIS | 1 | SET
25.031 | Motor for disconnector switches and grounding switches for 245KV GIS | 1 | SET
25.032 | Complete drive mechanism for fast acting grounding switches for 245KV GIS | 1 | SET
25.033 | Covers with all accessories necessary to close a compartment in case of dismantling of any part of the enclosure to ensure the sealing of that compartment | 3 | No.
25.034 | Motor for fast acting grounding switches for 245KV GIS | 1 | SET
25.035 | Rupture disc for circuit breakers / potential transformer for 245KV GIS (2 nos. of each type) | 1 | SET
25.036 | Rupture disc for other compartments for 245KV GIS | 1 | SET
25.037 | Limit switch & Aux Switch for 245KV GIS | 1 | SET
25.038 | Bus supplort insulator of each type for 245KV GIS | 1 | SET
25.03 | For 36KV INDOOR AIS
25.031 | 1250A, VCB complete with operating mechanism | 1 | SET
25.032 | Trip Coil | 8 | No.
25.04 | For 220/33KV,100MVA Transformers
25.041 | 245kV H.V. Bushing witj metal parts and Gaskets | 1 | No.
25.042 | HV side neutral bushing | 1 | No.
25.043 | 36KV LV bushing | 1 | No.
25.044 | 36kV Neutral Bushing with metal parts and gaskets | 1 | No.
25.045 | Local and remote winding temperature indicators with alarm and trip contacts and maximum reading pointer | 1 | SET
25.046 | Oil temperature indictor with alarm and trip contacts and maximum reading pointer | 1 | SET
25.047 | Pressure relief device for main tank | 1 | No.
25.048 | Pressure relief device for OLTC | 1 | No.
25.049 | Silica Gel/ Maintenance free breather | 1 | No.
25.05 | Magnetic oil level gauge with low oil level alarm contacts | 1 | No.
25.051 | Oil flow indicator with contacts | 1 | No.
25.052 | Cooler pump with motor | 1 | No.
25.053 | Cooler fan with motor. | 1 | No.
25.054 | Buchholz relay. | 1 | No.
25.055 | Tap position Indicator (Local and remote) | 1 | No.
25.056 | Oil sampling bottle | 3 | No.
25.057 | Oil Surge Relay | 1 | No.
25.05 | 220KV Control and Relay Panel
25.051 | Over current and Earth fault relay | 1 | No.
25.052 | Distance Protection relay | 1 | No.
25.053 | Differential relay | 1 | No.
25.054 | Mater Trip relay | 1 | No.
25.055 | Trip Circuit Supervision relay | 1 | No.
25.06 | For 33KV Control and Relay Panel
25.061 | Over current and Earth fault relay | 1 | No
25.062 | Distance Protection relay | 1 | No
25.063 | Differential relay | 1 | No
25.064 | Mater Trip relay | 1 | No
25.065 | Trip Circuit Supervision relay | 1 | No
25.07 | For PLCC | 1 | LOT
25.08 | For FOTE | 1 | LOT
25.09 | For Cable Termination Kit | 2 | Nos
26 | Testing Kit for Transformers
26.01 | Automatic Transformer Oil BDV Testing Kit | 1 | Set
26.02 | Oil Storage Tank - 20kL Capacity | 1 | Set
26.03 | Stainless Steel Oil sampling bottle (One Litre Capacity) | 1 | Set
26.04 | Syringes for sampling oil | 1 | Set
27 | ESMP Requirement
27.01 | Personal protective equipment’s (Hard hats (with full/partial brims as necessary) Safety glasses with side shields. Face masks/shields. Suitable footwear (safety/steel-toed boots, rated dielectric footwear) Insulating gloves (rated, used along with leather/cloth linings for shock protection)) as per site requirement | 1 | Lot
27.02 | SF6 retrieving arrangement as per site requirement | 1 | Lot
27.03 | Wire insulation/ Bird Deflectors/ Bird Flapper as per requirement including installation | 1 | Lot
Total in Figures
Quoted Rate in Figures |  |  | Select