## ANNEXURE XII_TS
ANNEXURE-X:
TOWER SCHEDULE FOR ASSOCIATED TRANSMISSION LINE FOR 220/33KV CHAYGAON GIS
SL NO | AP NO | TOWER NO | TYPE OF TOWER | EXTENTION | REMARKS | ANGLE OF DEVIATION | SPAN IN (M) | SEC. LENG. | CUMLTV LENGTH | R.L | C.P.D. | LEVEL DIFF. | Sum of Adj. Span | WEIGHT SPAN IN (HOT) |  |  | WEIGHT SPAN IN (COLD) |  |  | TYPE OF FDN | MAJOR CROSSING DETAIL | VILLAGE NAME | GPS READING (WGS 84)
[14 empty] | LEFT | RIGHT | TOTAL | LEFT | RIGHT | TOTAL
[23 empty] | NORTHING | EASTING
1 | EXT-235 | EXT-235 | DC+0 | 0 |  | 18°55'38"RT |  |  |  | 46.5 | 0 |  | 29 |  | -109.4199 | -109.4199 |  | -226.8373 | -226.8373 |  |  | 2NO JAMBARI | 91°16'5.6'' | 26°2'28.5''
[7 empty] | 29 |  |  |  |  | 1.98
2 | 1 | 1/0 | DD+3 | 3 |  | 51°31'31"RT |  | 29 | 29 | 45.48 | 0 |  | 203 | 138.4199 | -41.1966 | 97.2233 | 255.8373 | -162.6663 | 93.171 |  |  | 2NO JAMBARI | 91°16'5.4'' | 26°2'29.4''
[7 empty] | 174 |  |  |  |  | 12.29 | [8 empty] | Pond
3 | 2 | 2/0 | DD+15 | 15 |  | 21°54'59"LT |  | 174 | 203 | 45.77 | 0 |  | 330 | 215.1966 | 42.0493 | 257.2459 | 336.6663 | 7.985 | 344.6513 |  |  | 2NO JAMBARI | 91°16'9.5'' | 26°2'33.6''
[7 empty] | 156 |  |  |  |  | 3.09 | [8 empty] | Proposed 132KV Boko to Chaygaon TL.
4 | 3 | 3/0 | DD+18 | 18 |  | 56°31'50"RT |  | 156 | 359 | 45.86 | 0 |  | 466 | 113.9507 | 225.726 | 339.6767 | 148.015 | 292.7408 | 440.7558 |  |  | 2NO JAMBARI | 91°16'11.3'' | 26°2'38.5''
[7 empty] | 310 |  |  |  |  | -12.08 | [8 empty] | Nala
5 |  | 3/1 | DB+6 | 6 |  |  |  | 310 | 669 | 45.78 | 0 |  | 636 | 84.274 | 169.6253 | 253.8993 | 17.2592 | 175.9029 | 193.1621 |  |  | 2NO JAMBARI
[7 empty] | 326 |  |  |  |  | -1.19 | [8 empty] | 4 Nos 11KV,33KV,2 Nos FP, 2 Nos Pond, Factory Boundary
6 | 4 | 4/0 | DC+6 | 6 |  | 23°38'29"LT |  | 326 | 995 | 44.59 | 0 |  | 547 | 156.3747 | 149.1814 | 305.5562 | 150.0971 | 185.8331 | 335.9302 |  |  | 2NO JAMBARI | 91°16'33.5'' | 26°2'43.6''
[7 empty] | 221 |  |  |  |  | -4.71 | [8 empty] | 2 Nos Pond, 11KV
7 | 5 | 5/0 | DD+0 | 0 |  | 55°3'54"LT |  | 221 | 1216 | 45.88 | 0 |  | 416 | 71.8186 | 99.1754 | 170.9939 | 35.1669 | 100.7628 | 135.9297 |  |  | 2NO JAMBARI | 91°16'39.7'' | 26°2'48''
[7 empty] | 195 |  |  |  |  | -0.18 | [8 empty] | 2 Nos Pond, 11KV
8 | 6 | 6/0 | DD+0 | 0 |  | 49°16'7"LT |  | 195 | 1411 | 45.7 | 0 |  | 324 | 95.8246 | 61.8268 | 157.6514 | 94.2372 | 59.2938 | 153.531 |  |  | 2NO JAMBARI | 91°16'39.3'' | 26°2'54.3''
[7 empty] | 129 |  |  |  |  | 0.19 | [8 empty] | Cemetery Area
9 | 7 | 7/0 | DD+0 | 0 |  | 9°32'22"LT |  | 129 | 1540 | 45.89 | 0 |  | 208 | 67.1732 | 40.1892 | 107.3625 | 69.7062 | 40.8423 | 110.5485 |  |  | 2NO JAMBARI | 91°16'35.7'' | 26°2'56.9''
[7 empty] | 79 |  |  |  |  | -0.03 | [8 empty] | Factorty Boundary, Pond, Cemetery, Cemetery Area.
10 | BAY | BAY | GANTRY | 0 |  |  |  | 79 | 1619 | 45.86 | 0 |  | 79 | 38.8108 |  | 38.8108 | 38.1577 |  | 38.1577 |  |  | 2NO JAMBARI | 91°16'33.2'' | 26°2'58''

## ANNEXURE IX_SUPPLY
Item No | Description | Measurement | Nos. of towers | Guranteed MT/CuM per tower | Actual MT/CuM per tower | Approved MT/CuM per tower | Provisional Quantity
Unit
1.0 | TOWER AND TOWER ACCESSORIES
1.1. | Tangent towers (A type)
(a) Superstructures
| (i) Galvanized steel works including hangers, gussets, strain plates etc. (No of Tower X MT* per Tower) | MT | 1 | 4.194 |  |  | 4.194
| (ii) Galvanized iron nuts & bolts, spring washers, step bolts etc. (No of Tower X MT* per Tower) | MT | 1 | 0.177 |  |  | 0.177
(b) Stub set of four
| (i) Partially galvanized stub angle | Set | 1 |  |  |  | 1
| (ii) Galvanized iron nuts & bolts, spring washers, step bolts etc. | Lot per Set | 1 |  |  |  | 1
1.2. | Angle towers (B type)
(a) Superstructures
| (i) Galvanized steel works including hangers, gussets, strain plates etc. (No of Tower X MT* per Tower) | MT | 3 | 6.055 |  |  | 18.165
| (ii) Galvanized iron nuts & bolts, spring washers, step bolts etc. (No of Tower X MT* per Tower) | MT | 3 | 0.262 |  |  | 0.786
(b) Stub set of four
| (i) Partially galvanized stub angle | Set | 0 |  |  |  | 0
| (ii) Galvanized iron nuts & bolts, spring washers, step bolts etc. | Lot per Set | 0 |  |  |  | 0
1.3. | Angle towers (C type)
(a) Superstructures
| (i) Galvanized steel works including hangers, gussets, strain plates etc. (No of Tower X MT* per Tower) | MT | 1 | 7.379 |  |  | 7.379
| (ii) Galvanized iron nuts & bolts, spring washers, step bolts etc. (No of Tower X MT* per Tower) | MT | 1 | 0.315 |  |  | 0.315
(b) Stub set of four
| (i) Partially galvanized stub angle | Set per Tower | 1 |  |  |  | 1
| (ii) Galvanized iron nuts & bolts, spring washers, step bolts etc. | Lot per Set | 1 |  |  |  | 1
1.4. | Angle towers (D type)
(a) Superstructures
| (i) Galvanized steel works including hangers, gussets, strain plates etc. (No of Tower x MT* per Tower) | MT | 5 | 8.557 |  |  | 42.785
| (ii) Galvanized | MT | 5 | 0.34 |  |  | 1.7
iron nuts & bolts, spring washers, step bolts etc.
(b) Stub set of four
| (i) Partially galvanized stub angle | Set per Tower | 2 |  |  |  | 2
| (ii) Galvanized iron nuts & bolts, spring washers, step bolts etc. | Lot per Set | 2 |  |  |  | 2
1.5. | 3 Meter Extension Body
(A) Superstructures
(a) Galvanized steel works including hangers, gussets, strain plates etc. (No of Body x MT* per Tower)
| (i) A type | MT | 0 | 0.78 |  |  | 0
| (ii) B type | MT | 1 | 1.063 |  |  | 1.063
| (iii) C type | MT | 0 | 1.297 |  |  | 0
| (iv) D-type | MT | 1 | 1.529 |  |  | 1.529
(b) Galvanized iron nuts & bolts, spring washers, step bolts etc. (No of Tower x MT* per Tower)
| (i) A type | MT | 0 | 0.03 |  |  | 0
| (ii) B type | MT | 1 | 0.034 |  |  | 0.034
| (iii) C type | MT | 0 | 0.042 |  |  | 0
| (iv) D-type | MT | 1 | 0.05 |  |  | 0.05
(B) Stub set of four
| (a) Partially galvanized stub angle. | [5 empty] | 0
| (i) A type | Set | 0 |  |  |  | 1
| (ii) B type | Set | 1 |  |  |  | 0
| (iii) C type | Set | 0 |  |  |  | 1
| (iv) D-type | Set | 1
(b) Galvanized iron nuts & bolts, spring washers, step bolts etc.
| (i) A type | Lot per Set | 0 |  |  |  | 0
| (ii) B type | Lot per Set | 1 |  |  |  | 1
| (iii) C type | Lot per Set | 0 |  |  |  | 0
| (iv) D-type | Lot per Set | 1 |  |  |  | 1
1.6. | 6 Meter Extension Body,
(A) Superstructures
(a) Galvanized steel works including hangers, gussets, strain plates etc. (No of Tower x MT* per Body)
| (i) A type | MT | 0 | 1.425 |  |  | 0
| (ii) B type | MT | 2 | 1.9 |  |  | 3.8
| (iii) C type | MT | 0 | 2.34 |  |  | 0
| (iv) D-type | MT | 1 | 2.739 |  |  | 2.739
(b) Galvanized iron nuts & bolts, spring washers, step bolts etc. (No of Tower x MT* per Body)
| (i) A type | MT | 0 | 0.05 |  |  | 0
| (ii) B type | MT | 2 | 0.068 |  |  | 0.136
| (iii) C type | MT | 0 | 0.074 |  |  | 0
| (iv) D-type | MT | 1 | 0.085 |  |  | 0.085
(B) Stub set of four
(a) Partially galvanized stub angle.
| (i) A type | Set | 0 |  |  |  | 0
| (ii) B type | Set | 2 |  |  |  | 2
| (iii) C type | Set | 0 |  |  |  | 0
| (iv) D-type | Set | 1 |  |  |  | 1
(b) Galvanized iron nuts & bolts, spring washers, step bolts etc.
| (i) A type | Lot per Body | 0 |  |  |  | 0
| (ii) B type | Lot per Body | 2 |  |  |  | 2
| (iii) C type | Lot per Body | 0 |  |  |  | 0
| (iv) D-type | Lot per Body | 1 |  |  |  | 1
1.7. | 9 Meter Extension Body,
(A) Superstructures
(a) Galvanized steel works including hangers, gussets, strain plates etc. (No of Tower x MT* per Body)
| (i) A type | MT | 0 | 2.246 |  |  | 0
| (ii) B type | MT | 0 | 2.7 |  |  | 0
| (iii) C type | MT | 0 | 3.245 |  |  | 0
| (iv) D-type | MT | 1 | 3.803 |  |  | 3.803
(b) Galvanized iron nuts & bolts, spring washers, step bolts etc. (No of Tower x MT* per Body)
| (i) A type | MT | 0 | 0.08 |  |  | 0
| (ii) B type | MT | 0 | 0.091 |  |  | 0
| (iii) C type | MT | 0 | 0.098 |  |  | 0
| (iv) D-type | MT | 1 | 0.115 |  |  | 0.115
(B) Stub set of four
(a) Partially galvanized stub angle.
| (i) A type | Set | 0 |  |  |  | 0
| (ii) B type | Set | 0 |  |  |  | 0
| (iii) C type | Set | 0 |  |  |  | 0
| (iv) D-type | Set | 1 |  |  |  | 1
(b) Galvanized iron nuts & bolts, spring washers, step bolts etc.
| (i) A type | Lot per Body | 0 |  |  |  | 0
| (ii) B type | Lot per Body | 0 |  |  |  | 0
| (iii) C type | Lot per Body | 0 |  |  |  | 0
| (iv) D-type | Lot per Body | 1 |  |  |  | 1
1.8. | (a) Adjustable Stub setting template
| (i) A type | Set |  |  |  |  | 1
| (ii) B type | Set |  |  |  |  | 1
| (iii) C type | Set |  |  |  |  | 1
| (iv) D type | Set |  |  |  |  | 2
(b) Galvanized bolts & buts for above template
| (i) A type | Lot |  |  |  |  | 1
| (ii) B type | Lot |  |  |  |  | 1
| (iii) C type | Lot |  |  |  |  | 1
| (iv) D type | Lot |  |  |  |  | 2
1.9 | Procurement of Danger plates. | No |  |  |  |  | 10
1.10. | Procurement of Phase plates.(Set of Three) | No |  |  |  |  | 20
1.11 | Procurement of Number plates. | No |  |  |  |  | 10
1.12 | Procurement of Bird guard. (Set of Three) | No |  |  |  |  | 2
1.13 | Procurement of anti climbing device | Set |  |  |  |  | 10
1.14 | Procurement of Circuit Plate | No |  |  |  |  | 10
2.0 | 37/4.00 mm All Aluminium Alloy Conductor | kM |  |  |  |  | 17
3.0 | POWER CONDUCTOR ACCESSORIES
3.1. | Stock bridge type Vibration Damper | No |  |  |  |  | 235
3.2. | Preformed Armoured Rods | No |  |  |  |  | 7
3.3 | Mid Span Compression Joint for Conductor | No |  |  |  |  | 9
3.4 | Repair Sleeve for Conductor | No |  |  |  |  | 5
4.0 | FIBRE OPTIC CABLES
4.1 | 48 Fibre (DWSM)OPGW Fibre Optic cable | km |  |  |  |  | 3
4.2 | Fibre Optic Approach Cable (DWSM48F) | km |  |  |  |  | 1
5 | OPGW HARDWARE/FITTINGS AND TERMINATIONS
5.1. | OPGW Suspension Assembly with twisted link c/w pre-formed armour rods and tower bond clamps | Set |  |  |  |  | 6
5.2 | OPGW Suspension Assembly with chain link c/w pre-formed armour rods and tower bond clamps | Set |  |  |  |  | 3
5.3 | OPGW double tension pass through assembly | Set |  |  |  |  | 2
5.4 | OPGW double tension assembly for splicing location c/w pre-formed armour rods and tower bond clamps | Set |  |  |  |  | 2
5.5 | OPGW Tension Single Dead end set for termination/ run in c/w pre-formed armour ros and tower bond clamps | Set |  |  |  |  | 3
5.6 | OPGW Vibration Damper c/w pre-formed armour rods | Set |  |  |  |  | 32
5.7 | Down Lead Clamp | Set |  |  |  |  | 2
5.8 | OPGW Optical Splice Kit (48 Fibre) including junction box | Set |  |  |  |  | 1
5.9 | OPGW Optical interface joint kit and junction for line/sub interface on substation gantries | Set |  |  |  |  | 1
6 | FODP
6.1 | FODP 48F: Indoor type, rack mounted with FCPC coupling and pig tails | Set |  |  |  |  | 2
7 | Installation hardware set for above 48Fibre, Fibre Optic Approach cableties/clips/cleats, conduits, ducts, supports,fittings, accessories etc for extending OPGW from sub station end tower/gantry to FODP at control/communication room by splicing fibres of OPGW with FOAC in joint box at tower/gantry and splicing FOAC in FODP at control/communication room. | Lot |  |  |  |  | 1
8 | Supply of following Aviation Requirements
8.1 | Span Markers | No |  |  |  |  | 9
9 | Obstruction Lights (to be provided as per IS 5613)
9.1 | (i) 1 Medium Intensity + 2 Low Intensity | [5 empty] | 10
9.2 | (ii) 1 Medium Intensity + 4 Low Intensity
10 | INSULATORS AND INSULATOR STRING HARDWARE
10.1 | 120 KN, 15 disc tension insulator string complete with all hardware fittings including tension clamp for AAAC ‘Zebra’ equivalent. | Set |  |  |  |  | 93
10.2 | 90 KN, 14 disc suspension insulator string complete with all hardware fittings including suspension clamp for AAAC ‘Zebra’ equivalent. | Set |  |  |  |  | 7
10.3 | 240 KN, double tension insulator string comprising of 2 strings of 120 KN Disc insulators (15 Disc per String) complete with all hardware fittings including tension clamp for AAAC ‘Zebra’ equivalent. | Set |  |  |  |  | 25
NOTE: 3% extra considered for all Hardware fiitings and insulator strings

## ANNEXURE X_ERECTION
Item No | Description | Measurement Unit | Nos. of towers | Guranteed MT/CuM per tower | Actual MT/CuM per tower | Approved MT/CuM per tower | Provisional Quantity
1.0 | Setting of stubs (sets of four) including transportation and distribution of stubs and accessories from store to site excluding cost of excavation, concreting and back filling
1.1. For Normal tower :
| (i) Suspension tower A type : | Set |  |  |  |  | 1
| (ii) Angle tower B type | Set |  |  |  |  | 0
| (iii) Angle tower C type | Set |  |  |  |  | 1
| (iv) Angle tower D type | Set |  |  |  |  | 2
1.2. For Towers with 3 meter extension
| (i) A type | Set |  |  |  |  | 0
| (ii) B type | Set |  |  |  |  | 1
| (iii) C type | Set |  |  |  |  | 0
| (iv) D type | Set |  |  |  |  | 1
1.3. For Towers with 6 meter extension
| (i) A type | Set |  |  |  |  | 0
| (ii) B type | Set |  |  |  |  | 2
| (iii) C type | Set |  |  |  |  | 0
| (iv) D type | Set |  |  |  |  | 1
1.4. For Towers with 9 meter extension
| (i) A type | Set |  |  |  |  | 0
| (ii) B type | Set |  |  |  |  | 0
| (iii) C type | Set |  |  |  |  | 0
| (iv) D type | Set |  |  |  |  | 1
2.0 | Super structure erection including transportation of structures by any means and distribution of structure and accessories from stores to site excluding fixing of Danger plate, number plate, anti climbing device, hoisting of insulators and paintings, if any as per direction of site Engineer.
2.1. Normal tower (No of Tower x MT* )
| (i) Suspension tower A type : | MT | 1 | 4.364 |  |  | 4.364
| (ii) Angle tower B type | MT | 0 | 6.34 |  |  | 0
| (iii) Angle tower C type | MT | 1 | 7.728 |  |  | 7.728
| (iv) Angle tower D type | MT | 2 | 8.933 |  |  | 17.866
2.2. 3 meter Extension Body (No of Tower x MT* )
| (i) A type | MT | 0 | 0.81 |  |  | 0
| (ii) B type | MT | 1 | 1.098 |  |  | 1.098
| (iii) C type | MT | 0 | 1.338 |  |  | 0
| (iv) D type | MT | 1 | 1.578 |  |  | 1.578
2.3. 6 meter Extension Body
| (i) A type | MT | 0 | 1.475 |  |  | 0
| (ii) B type | MT | 2 | 1.975 |  |  | 3.95
| (iii) C type | MT | 0 | 2.413 |  |  | 0
| (iv) D type | MT | 1 | 2.823 |  |  | 2.823
2.4. 9 meter Extension Body
| (i) A type | MT | 0 | 2.333 |  |  | 0
| (ii) B type | MT | 0 | 2.805 |  |  | 0
| (iii) C type | MT | 0 | 3.343 |  |  | 0
| (iv) D type | MT | 1 | 3.922 |  |  | 3.922
3.0 | Stringing of power conductors including transportation from Stores and distribution of conductors and accessories to sites and laying, stringing, tensioning , clamping, jointing, jumpering and hoisting of insulators complete including cost of all fittings and accessories not specifically mentioned elsewhere per route Km (6 conductors for Double Circuit Line) of line. | Route KM |  |  |  |  | 2.715
4.0 | Grounding of towers with 3 metre long 25 mm dia G I pipe, including cost of all materials, such as GI pipes, GI bolts & nuts and washer, salt, coke etc as per Specification. | Per Tower. |  |  |  |  | 10 | *no of towers
5.0. | Painting of towers with bituminous paints of approved quality up to 3 metres from ground level including the cost of paints. | Per Tower |  |  |  |  | 10 | *no of towers
6.0. | Erection of Danger plates. (1 no per tower) | Nos |  |  |  |  | 10
7.0. | Erection of Phase plates. (6 nos per tower per tower as required) | Sets |  |  |  |  | 10
8.0. | Erection of Number plates. (1 no per tower) | Nos |  |  |  |  | 10
9.0. | Erection of Bird guard. (6 nos per tower as required) | Sets |  |  |  |  | 1 | *only for S tower
10.0. | Erection of anti climbing device (1 set per tower) | Sets |  |  |  |  | 10
11.0. | Erection of Circuit Plate | No |  |  |  |  | 10
12.0 | Check Survey as per Specification | Route Km |  |  |  |  | 2.715
13.0 | Welding of all nuts & bolts up to the bottom cross arm level including all charges of transportation, materials etc.
| (i) A+0 type | No |  |  |  |  | 1
| (ii) B+0 type | No |  |  |  |  | 0
| (iii) C+0 type | No |  |  |  |  | 1
| (iv) D+0 type | No |  |  |  |  | 2
| (v) A+3 type | No |  |  |  |  | 0
| (vi) B+3 type | No |  |  |  |  | 1
| (vii) C+3 type | No |  |  |  |  | 0
| (viii) D+3 type | No |  |  |  |  | 1
| (ix) A+6 type | No |  |  |  |  | 0
| (x) B+6 type | No |  |  |  |  | 2
| (xi) C+6 type | No |  |  |  |  | 0
| (xii) D+6 type | No |  |  |  |  | 1
| (xiii) A+9 type | No |  |  |  |  | 0
| (xiv) B+9 type | No |  |  |  |  | 0
| (xv) C+9 type | No |  |  |  |  | 0
| (xvi) D+9 type | No |  |  |  |  | 1
14.0 | Concreting of foundation including all Labour, materials, equipment, excavation shuttering, head loading, back filling etc complete for handling, transportation, batching, mixing, placing, levelling, curing etc complete inclusive of cost of cement and reinforcement steel.
14.1. For A Type Tower (No of Tower x CuM* )
| (i) Dry Type Foundation | CUM | 0 | 6.8 |  |  | 0
| (ii) Wet Type foundation | CUM | 1 | 9.222 |  |  | 9.222
| (iii) Semi submerged Type | CUM | 0 | 11.434 |  |  | 0
| (iv) Submerged Type | CUM | 0 | 14.062 |  |  | 0
| 14.2. For B+3 Type Tower(No of Tower x CuM* ) | [5 empty] | 0
| (i) Dry Type Foundation | CUM | 0 | 17.43 |  |  | 0
| (ii) Wet Type foundation | CUM | 1 | 19.543 |  |  | 19.543
| (iii) Semi submerged Type | CUM | 0 | 23.14 |  |  | 0
| (iv) Submerged Type | CUM | 0 | 28.52 |  |  | 0
| 14.3. For B+6 Type Tower(No of Tower x CuM* ) | [5 empty] | 0
| (i) Dry Type Foundation | CUM | 0 | 17.43 |  |  | 0
| (ii) Wet Type foundation | CUM | 1 | 20.12 |  |  | 20.12
| (iii) Semi submerged Type | CUM | 1 | 23.14 |  |  | 23.14
| (iv) Submerged Type | CUM | 0 | 28.52 |  |  | 0
| 14.4. For C Type Tower(No of Tower x CuM* ) | [5 empty] | 0
| (i) Dry Type Foundation | CUM | 0 | 19.18 |  |  | 0
| (ii) Wet Type foundation | CUM | 1 | 22.075 |  |  | 22.075
| (iii) Semi submerged Type | CUM | 0 | 26.751 |  |  | 0
| (iv) Submerged Type | CUM | 0 | 33.551 |  |  | 0
| 14.5. For D Type Tower(No of Tower x CuM* ) | [5 empty] | 0
| (i) Dry Type Foundation | CUM | 0 | 23.88 |  |  | 0
| (ii) Wet Type foundation | CUM | 2 | 29.004 |  |  | 58.008
| (iii) Semi submerged Type | CUM | 0 | 35.132 |  |  | 0
| (iv) Submerged Type | CUM | 0 | 43.908 |  |  | 0
| 14.6. For D+3 Type Tower(No of Tower x CuM* ) | [5 empty] | 0
| (i) Dry Type Foundation | CUM | 0 | 23.88 |  |  | 0
| (ii)Wet Type foundation | CUM | 1 | 31.345 |  |  | 31.345
| (iii) Semi submerged Type | CUM | 0 | 37.473 |  |  | 0
| (iv) Submerged Type | CUM | 0 | 46.249 |  |  | 0
| 14.7. For D+6 Type Tower(No of Tower x CuM* ) | [5 empty] | 0
| (i) Dry Type Foundation | CUM | 0 | 23.88 |  |  | 0
| (ii) Wet Type foundation | CUM | 1 | 33.12 |  |  | 33.12
| (iii) Semi submerged Type | CUM | 0 | 38.33 |  |  | 0
| (iv) Submerged Type | CUM | 0 | 48.529 |  |  | 0
| 14.8. For D+9 Type Tower(No of Tower x CuM* ) | [5 empty] | 0
| (i) Dry Type Foundation | CUM | 0 | 23.88 |  |  | 0
| (ii) Wet Type foundation | CUM | 1 | 33.12 |  |  | 33.12
| (iii) Semi submerged Type | CUM | 0 | 38.33 |  |  | 0
| (iv) Submerged Type | CUM | 0 | 48.69 |  |  | 0
15.0. | OPGW
15.1. | OPGW cable & characteristic
| Stringing of 48 Fibre (DWSM)OPGW Fibre Optic cable including transportation and distribution of OPGW and accessories to site and laying, stringing, tensioning , clamping, jointing , complete including all fittings and accessories not specifically mentioned elsewhere per route Km of line | Route KM |  |  |  |  | 2.715
| Installation of Hardware set for above 48 Fibre OPGW Fibre Optic cabling including all cable fittings & accessories like suspension assembly, tension assembly, dead end tension assembly at line terminations, tension double end set for splice location, vibration dampers, earthing clamps, down lead clamps, in-line spice enclosures etc. | LS |  |  |  |  | 1
| Joint box (48 Fibre) | No. |  |  |  |  | 1
15.2. | Installation of FODP
| FODP 48F : Indoor Type, rack mounted with FCPC coupling and pig tails | No. |  |  |  |  | 1
15.3. | Fibre Optic approach cable (DWSM 48F)
| Installation of 48 Fibre (DWSM) Fibre Optic approach cable | Km. |  |  |  |  | 1
| Installation of hardware set for above 48 Fibre, Fibre Optic Approach Cable ties/clips/cleats, conduits, ducts, supports, fittings, accessories etc for extending OPGW from sub-station end tower/gantry to FODP at control/ communication room by splicing fibres of OPGW with FOAC in joint box at tower/gantry and splicing FOAC in FODP at control/ communication room. | Set |  |  |  |  | 1
16.0. | Installation of Span Markers | Nos |  |  |  |  | 9
17.0. | Installation of Obstruction Lights (to be provided as per IS 5613)
| (i) 1 Medium Intensity + 2 Low Intensity | Nos |  |  |  |  | 10
| (ii) 1 Medium Intensity + 4 Low Intensity | Nos